噪声管理制度

Noise Management System

内部使用

在使用前，请和文档编写人员确认本文档为最新版本。

未经上海暻熠数据科技有限公司、上海暻耀网络技术有限公司书面许可，其它任何机构或个人不可传阅、引用或复制本文件的内容。

Internal use

Before using, check with the documentation writer to make sure this document is the latest version.

Without the written permission of Shanghai Jingyi Data Technology Co., Ltd., Shanghai Jingyao internet Technology Co., Ltd., no other organization or individual is allowed to circulate, quote or copy the content of this document.

| 文件编号 Documents | IP-PJ-EHS-27 |
| --- | --- |
| 版 本 Edition | V1.0 |
| 文件维护部门 File maintenance department | 上海浦江数据中心 |
| 会签部门 Document Signing department | 上海浦江数据中心 |
| 执行范围 Scope of execution | 上海浦江数据中心 |

文件修订记录

Document revision record

| 版本号 Edition | 版本日期 Date | 修订内容 Revised Content | 修订人员 Revision personnel | 核准员 Approver | 备注 Remark |
| --- | --- | --- | --- | --- | --- |
| V1.0 | 2025-04-16 | 首次修订 | 楚靖岳 | 陆磊 |  |

目录 Content

1目的 Purpose	4

2适用范围	4

3规范性引用文件	4

4术语和定义 Terms and definitions	4

5 职责 Duties	5

5.1 采购部门 Purchasing department	5

5.2 设备运维部门 Operation and maintenance department	5

5.3 EHS管理负责人 The EHS officer	5

6 程序 Procedures	6

6.1 噪声来源 Sources of noise	6

6.2 厂界噪声控制措施 Plant boundary noise control measures	6

6.3 厂界噪声监测 Factory boundary noise monitoring	8

6.4 厂界噪声排放限值 Factory boundary noise emission limits	8

6.5 测量方法 Measurement method	10

6.6 应急响应 Emergency response	10

6.7 培训 Training	11

6.8 审核与审查 Audit and review	11

7 附件Attachments	11

1目的 Purpose

本制度旨在建立上海暻熠数据科技有限公司、上海暻耀网络技术有限公司（以下简称“上海浦江数据中心”）噪声管理流程。目标包括确保遵守国家和地方法律法规、国外相关法规、客户要求以及上海浦江数据中心内部要求，确保噪声管理合规，降低运营EHS风险，并促进持续改进。

This system aims to establish the noise management process of Shanghai Jingyi Data Technology Co., Ltd., Shanghai Jingyao internet Technology Co., Ltd.. (hereinafter referred to as "SHANGHAI Pujiang Data Center"). Objectives include ensuring compliance with national and local laws and regulations, relevant foreign regulations, customer requirements, and internal requirements of SHANGHAI PUJIANG Data Center, ensuring noise management compliance, reducing operational EHS risks, and promoting continuous improvement.

2适用范围 Scope of application

适用于上海浦江数据中心，以及所有与EHS有关事项的管理职能部门。

Applicable to SHANGHAI PUJIANG Data Center and all management functions related to EHS.

3规范性引用文件 Reference documents

《中华人民共和国噪声污染防治法》（2022年6月5日起实施）

Law of the People's Republic of China on the Prevention and Control of Noise Pollution (effective June 5, 2022)

GB 12348  工业企业厂界环境噪声排放标准

GB 12348 Environmental noise emission standard for factory boundaries of industrial enterprises

GB 12523  建筑施工厂界环境噪声排放标准

GB 12523 Environmental noise emission standard for building construction plant boundary

HJ 819 排污单位自行监测技术指南 总则

HJ 819	 Technical Guidelines for self-monitoring of pollutant discharge units

4术语和定义 Terms and definitions

4.1噪声 Noise

指在工业生产、建筑施工、交通运输和社会生活中产生的干扰周围生活环境的声音。

Refers to the sound produced in industrial production, building construction, transportation and social life that disturbs the surrounding living environment.

4.2噪声污染 Noise pollution

指超过噪声排放标准或者未依法采取防控措施产生噪声，并干扰他人正常生活、工作和学习的现象。

Refers to the phenomenon of exceeding noise emission standards or failing to take prevention and control measures in accordance with law to produce noise and interfere with the normal life, work and study of others.

4.3工业企业厂界环境噪声 Environmental noise at the factory boundary of industrial enterprises

指在工业生产活动中使用固定设备等产生的、在厂界处进行测量和控制的干扰周围生活环境的声音。

4.4昼间和夜间 Daytime and nighttime

根据《中华人民共和国环境噪声污染防治法》，“昼间”是指6:00至22:00之间的时段；“夜间”是指22:00至次日6:00之间的时段。

According to the Law of the People's Republic of China on the Prevention and Control of Environmental Noise Pollution, "daytime" means the period between 6:00 and 22:00; And "night" refers to the time period between 22:00 and 6:00 the next day.

5 职责 Duties

## 5.1 采购部门 Purchasing department

5.1.1与有资质的监测企业签订噪声监测合同。

Sign a noise monitoring contract with a qualified monitoring enterprise.

## 5.2 设备运维部门 Operation and maintenance department

5.2.1设备运维人员对噪声控制设施和装置进行维护与检查。

Equipment operation and maintenance personnel shall maintain and inspect noise control facilities and devices.

5.2.2设备运维人员对设备噪声异常信息进行报告。

Equipment operation and maintenance personnel shall report abnormal noise information of equipment.

## 5.3 EHS管理负责人 EHS Officer

5.3.1制定、审查并定期更新本程序。

Develop, review and regularly update this procedure.

5.3.2确定并更新所有适用的环境噪声排放管理条例和标准。

Determine and update all applicable regulations and standards for the management of environmental noise emissions.

5.3.3识别导致厂界噪声排放的噪声源。

Identify noise sources that contribute to plant boundary noise emissions.

5.3.4制定上海浦江数据中心噪声监测计划，并组织上海浦江数据中心开展监测。

Formulate noise monitoring plan for SHANGHAI PUJINAG Data Center, and organize SHANGHAI PUJIANG Data center to carry out monitoring.

5.3.5对异常噪声情况进行调查和响应。

Investigate and respond to abnormal noise.

5.3.6对负责操作和维护噪声相关设施、设备的相关团队成员进行在职培训。

Conduct on-the-job training for relevant team members responsible for the operation and maintenance of noise-related facilities and equipment.

6 程序 Procedures

## 6.1 噪声来源 Sources of noise

6.1.1 EHS管理负责人确定环境噪声源，并制定主要环境噪声源清单，定期更新《环境噪声源识别清单》，详见附件1。

The EHS officer shall determine environmental noise sources, formulate a list of major environmental noise sources, and update the Identification List of Environmental Noise Sources regularly, as shown in Attachment 1.

6.1.2上海浦江数据中心噪声源应包括但不限于:

Noise sources of SHANGHAI PUJIANG Data Center shall include but not be limited to:

- 由各种风机、空气压缩机、废气排放等产生的气动噪声。

Pneumatic noise generated by various fans, air compressors, exhaust gas emission, etc.

- 运行各种泵、空气压缩机、空调装置、电动工具和/或在维护和修理过程中涉及金属碰撞(如锤)的动作和接触所产生的机械噪声。

Mechanical noise from the operation of various pumps, air compressors, air conditioning units, power tools and/or actions and contacts involving metal collisions (such as hammers) during maintenance and repair.

- 发电机、变压器等设备产生的电磁噪声。

Electromagnetic noise generated by equipment such as generators, transformers, etc.

- 施工现场各种车辆、机械和设备混合产生的施噪声。

Construction noise generated by the mixture of various vehicles, machinery and equipment on the construction site.

## 6.2 厂界噪声控制措施 Plant boundary noise control measures

6.2.1工程噪声控制Engineering noise control:：

- 在设计阶段和机器设备采购之前，必须对噪声水平进行评估，并确保符合产品技术标准，特别是当其噪声是边界环境噪声水平的主要影响因素时。

At the design stage and before the purchase of machinery and equipment, the noise level must be assessed and the technical standards of the product must be ensured, especially when its noise is the main influence factor on the noise level of the boundary environment.

- 设备基础必须稳定可靠，防止因振动引起机械噪声。必要情况下，要为一些转动惯性大、转速高的设备增设隔音罩。

The foundation of the equipment must be stable and reliable to prevent mechanical noise caused by vibration. If necessary, soundproof enclosures should be added for some equipment with large rotational inertia and high rotational speed.

- 按照设计参数安装机器与设备。

Install machines and equipment according to design parameters.

- 定期检查噪声控制设备和装置，确保其正常运行。

Check noise control equipment and devices regularly to make sure they are working properly.

- 在新建、扩建或改造项目中，EHS管理负责人应对噪声控制措施评估，并确保这些设施与主要结构和设施同步设计、施工和调试。

In new construction, expansion, or renovation projects, the EHS officer shall assess noise control measures and ensure that these facilities are designed, constructed, and commissioned simultaneously with the main structures and systems.

- 在对当前具有高噪声排放的设备和装置进行重大变更时，上海浦江数据中心应评估变更对厂界噪声的影响，以确保合规。

When making major changes to current equipment and devices with high noise emissions, SHANGHAI PUJIANG Data Center shall assess the impact of the change on plant boundary noise to ensure compliance.

6.2.2操作噪声控制Operational Noise control:

- 操作人员应严格遵照相关规程来操作设备。

Operators should strictly follow the relevant rules to operate the equipment.。

- 一旦发现异常噪声情况，操作人员应及时向EHS管理负责人报告。

Once abnormal noise is found, the operator should report to the EHS officer in a timely manner.

- 如果异常噪声可能影响厂界噪声水平EHS管理负责人应及时安排专人进行维护。

If the abnormal noise may affect the noise level of the factory boundary, the EHS officer shall arrange special personnel to carry out maintenance in time.

- 设备运维人员应定期检查机器和设备的隔音装置，当隔音装置出现故障时，立即通知上海浦江数据中心EHS管理负责人。

The equipment operation and maintenance personnel shall check the sound insulation of the machine and equipment regularly, and notify the EHS officer of SHANGHAI PUJIANG Data Center immediately when the sound insulation device fails.

6.2.3施工噪声控制Construction noise control：

- 施工活动应在批准时段内进行，同时必须符合当地厂界噪声排放标准及公司内部要 求。

Construction activities shall be carried out within the approved time period, and must comply with the local plant boundary noise emission standards and the company's internal requirements.

- 数据中心及相关方应选择和使用市场上可获得的低噪声设备。在特定情况下，只有高噪声机器与设备可用时，应设计并安装额外的降噪和/或隔音装置，以降低噪声排放并确保符合厂界噪声标准。

The data center and related parties should select and use commercially available low noise equipment. In specific cases where only high noise machines and equipment are available, additional noise reduction and/or soundproofing should be designed and installed to reduce noise emissions and ensure compliance with plant boundary noise standards.

- 根据施工现场的实际情况，搅拌机等高噪声设备应尽量远离邻近社区。

Depending on the actual conditions at the construction site, high noise equipment such as mixers should be kept away from the adjacent community as much as possible.

- 施工机械高噪声作业时应合理安排在对周围环境影响最小的时段。

When the construction machinery works with high noise, it should be reasonably arranged in the period with the least impact on the surrounding environment.

## 6.3 厂界噪声监测 Factory boundary noise monitoring

6.3.1定期委托监测：根据环评文件要求、主管部门要求等从严开展定期检测，若无相关明确要求，厂界噪声每年至少开展一次监测。

Regular entrusted monitoring: regular testing shall be carried out strictly according to the requirements of EIA documents and competent authorities. If there is no specific requirement, the noise of plant boundary shall be monitored at least once a year.

6.3.2 EHS管理负责人应制定年度厂界噪声水平监测计划。

The EHS officer shall formulate an annual plant boundary noise level monitoring plan.

## 6.4 厂界噪声排放限值 Factory boundary noise emission limits

6.4.1 上海浦江数据中心日常运维时，厂界噪声执行《工业企业厂界环境噪声排放标准》（GB 12348）中下表1的限值标准。

During the daily operation and maintenance of SHANGHAI PUJIANG Data Center, the factory boundary noise shall comply with the limit standards in Table 1 below in the Emission Standard of Factory Boundary Environmental Noise for Industrial Enterprises (GB 12348).

表1厂界环境噪声排放限值  单位：分贝dB(A)

Table 1 Limits of environmental noise emission of factory boundary

| 厂界外声环境功能区类别 Category of aera outside plant | 时段 Time period |  |
| --- | --- | --- |
|  | 昼间 Day time | 夜间 Night |
| 0 | 50 | 40 |
| 1 | 55 | 45 |
| 2 | 60 | 50 |
| 3 | 65 | 55 |
| 4 | 70 | 55 |

6.4.2 声环境功能区分为以下五种类型。

Acoustic environmental functional areas are divided into the following five types.

0类声环境功能区:指康复疗养区等特别需要安静的区域。

Type 0 acoustic environment functional area: refers to the special need for quiet areas such as rehabilitation areas.

1类声环境功能区:指以居民住宅、医疗卫生、文化教育、科研设计、行政公为主要功能，需要保持安静的区域。

Type 1 acoustic environment functional area: refers to residential, medical and health, culture and education, scientific research and design, administrative public as the main functions, need to keep quiet area.

2类声环境功能区:指以商业金融、集市贸易为主要功能，或者居住、商业工业混杂，需要维护住宅安静的区域。

Type 2 acoustic environment functional areas: refers to commercial finance, market trade as the main function, or residential, commercial and industrial mix, need to maintain the quiet of residential areas.

3类声环境功能区:指以工业生产、仓储物流为主要功能，需要防止工业噪对周围环境产生严重影响的区域。

Type 3 acoustic environment functional area: refers to industrial production, warehousing and logistics as the main function, need to prevent industrial noise on the surrounding environment to have a serious impact on the area.

4类声环境功能区:指交通干线两侧一定距离之内，需要防止交通噪声对周围环境产生严重影响的区域。

Type 4 acoustic environment functional area: the area within a certain distance on both sides of major traffic arteries where it is necessary to prevent serious impact of traffic noise on the surrounding environment.

6.4.3 数据中心施工期间厂界噪声执行表2《建筑施工厂界环境噪声排放标准》（GB 12523）限值标准。

Factory boundary noise during data center construction Table 2 "Construction Factory Boundary Environmental Noise Emission Standard" (GB 12523) limit standards.

表2建筑施工场界环境噪声排放限值

Table 2 Environmental noise emission limits for the construction site boundary

| 时段 Time period | 昼间 Daytime | 夜间 Night |
| --- | --- | --- |
| 限值dB（A） | 70 | 55 |

## 6.5 测量方法 Measurement method

6.5.1上海浦江数据中心应委托监测单位应依据《工业企业厂界环境噪声排放标准》（GB 12348）要求的测量方法、测量位置等要求进行测量。

The monitoring unit entrusted by SHANGHAI PUJIANG Data Center shall carry out the measurement according to the measurement method, measurement position and other requirements as required in the Environmental Noise Emission Standard of Industrial Enterprise Boundary (GB 12348).

## 6.6 应急响应 Emergency response

6.6.1对周边社区噪声投诉进行调查，确定可能原因，并采取纠正性和预防性措施。上海浦江数据中心应与相关方进行沟通。

Investigate noise complaints from surrounding communities, determine possible causes, and take corrective and preventive measures. SHANGHAI PUJIANG Data Center shall communicate with relevant parties.

6.6.2一旦监测结果超出噪声排放限值，上海浦江数据中心应立即联合调查根本原因。找到原因后应制定并实施纠正性措施和预防性措施，直至将厂界噪声水平控制到限值以下。

Once the monitoring result exceeds the noise emission limit, SHANGHAI PUJIANG Data Center shall immediately jointly investigate the root cause. After finding the cause, corrective and preventive measures shall be formulated and implemented until the noise level within the factory boundary is controlled below the limit.

6.6.3受影响部门应严禁高噪声设备在异常状况下运行。

The affected department shall strictly prohibit the operation of high-noise equipment under abnormal conditions.

6.6.4如果噪声控制设备或设施被移除或出现故障，无论是暂时的还是永久的，应至少提前一周通知EHS管理负责人，以便在预计噪声排放可能超标时，向当地主管部门报备，以获得批准。

If noise control equipment or facilities are removed or malfunctioned, either temporarily or permanently, the EHS officer shall be notified at least one week in advance so that it can be reported to the local authority for approval if it is expected that noise emissions may exceed the standard.

## 6.7 培训 Training

6.7.1 EHS管理负责人应对上海浦江数据中心负责操作和维护噪声相关设施、设备的相关团队成员进行在职培训。

The EHS officer shall conduct on-the-job training for relevant team members who are responsible for operation and maintenance of noise-related facilities and equipment in SHANGHAI PUJIANG Data Center.

### 6.8 审核与审查 Audit and review

6.8.1设备运维部门应至少每月对噪声控制设施和装置进行一次检查，应采取预防性和纠正性措施。

The equipment operation and maintenance department shall inspect the noise control facilities and devices at least once a month and shall take preventive and corrective measures.

6.8.2 EHS管理负责人至少每年进行一次合规性审核，并建议预防性和纠正性措施。

The EHS officer shall conduct a compliance audit at least once a year and recommend preventive and corrective actions.

6.8.3 EHS管理负责人应每年审核一次本管理程序。

The EHS officer shall review this management procedure once a year.

7 附件Attachments

- IF-PJ-EHS-2701：环境噪声识别清单 Noise Identification List

环境噪声识别清单

Noise Identification List

| 编号 NO. | 噪声源 Source | 日期 Date | 时间 Time | 噪声水平（dB(A)） Noise Level | 备注 Remark |
| --- | --- | --- | --- | --- | --- |