废水管理制度

Sewage Management System

内部使用

在使用前，请和文档编写人员确认本文档为最新版本。

未经上海暻熠数据科技有限公司、上海暻耀网络技术有限公司书面许可，其它任何机构或个人不可传阅、引用或复制本文件的内容。

Internal use

Before using, check with the documentation writer to make sure this document is the latest version.

Without the written permission of Shanghai Jingyi Data Technology Co., Ltd., Shanghai Jingyao internet Technology Co., Ltd., no other organization or individual is allowed to circulate, quote or copy the content of this document.

| 文件编号 Documents | IP-PJ-EHS-28 |
| --- | --- |
| 版 本 Edition | V1.0 |
| 文件维护部门 File maintenance department | 上海浦江数据中心 |
| 会签部门 Document Signing department | 上海浦江数据中心 |
| 执行范围 Scope of execution | 上海浦江数据中心 |

文件修订记录

Document revision record

| 版本号 Edition | 版本日期 Date | 修订内容 Revised Content | 修订人员 Revision personnel | 核准员 Approver | 备注 Remark |
| --- | --- | --- | --- | --- | --- |
| V1.0 | 2025-04-16 | 首次修订 | 楚靖岳 | 陆磊 |  |

目录 Content

1 目的 Purpose	4

2 适用范围Scope of application	4

3 规范性引用文件 Refence documents	4

4 术语和定义 Terms and definitions	5

5 职责 Responsibilities	6

5.1废水设施运营部门 Sewage facility operation department	6

5.2采购部门 Purchasing department	6

5.3 EHS管理负责人 EHS officer	7

6 程序 Procedures	7

6.1 雨污分流 Seperation of rain and sewage	7

6.2废水污染源识别Identification of sewage pollution sources	8

6.3 污水处理系统Sewage treatment system	8

6.4 污水处理系统的日常维护	9

6.5 排污口规范化管理 Standardized management of sewage discharge outlets	9

6.6 水污染物监测 Water pollutant monitoring	10

6.7 废水排放应急预案 Emergency plan	12

6.8审核与审查 Audit and review	13

6.9文件管理 File management	13

7附件 Attachments	14

1 目的 Purpose

本制度旨在建立上海暻熠数据科技有限公司、上海暻耀网络技术有限公司（以下简称“上海浦江数据中心”）废水管理流程。目标包括确保遵守国家和地方法律法规、国外相关法规、客户要求以及上海浦江数据中心内部要求，确保废水管理合规，降低运营EHS风险，并促进持续改进。

The purpose of this system is to establish the sewage management process of Shanghai Jingyi Data Technology Co., Ltd., Shanghai Jingyao internet Technology Co., Ltd.. (hereinafter referred to as "SHANGHAI Pujiang Data Center"). Objectives include ensuring compliance with national and local laws and regulations, relevant foreign regulations, customer requirements, and internal requirements of SHANGHAI PUJIANG Data Center, ensuring compliance with sewage management, reducing operational EHS risks, and promoting continuous improvement.

2 适用范围Scope of application

适用于上海浦江数据中心，以及所有与EHS有关事项的管理职能部门。

Applicable to SHANGHAI PUJIANG Data Center and all management functions related to EHS.

3 规范性引用文件 Refence documents

《中华人民共和国环境保护法》（2014年修订）

Environmental Protection Law of the People's Republic of China (revised in 2014)

《中华人民共和国水污染防治法》（2017年修订）

Law of the People's Republic of China on Water Pollution Prevention and Control (revised in 2017)

《排污许可管理条例》（2021年3月1日起施行）

Regulations on the Administration of Pollutant Discharge Permits (effective March 1, 2021)

《排污许可管理办法》（2024年7月1日起施行）

Regulations on the Administration of Pollutant Discharge Permits (effective July 1, 2024)

GB 8978 污水综合排放标准

GB 8978 Comprehensive Sewage discharge standard

DB31/199-2018 上海市污水综合排放标准

DB31/199-2018 Shanghai Municipal Sewage Comprehensive Discharge Standard

GB 15562.1 环境保护图形标志—排放口（源）

GB 15562.1 Graphic sign for Environmental protection - Discharge outlet (source)

《关于印发排放口标志牌技术规格的通知》（环办【2003】95号）

Notice on Printing and distributing Technical Specifications of Discharge Port Signs (Environmental Affairs Office [2003] No. 95)

4 术语和定义 Terms and definitions

4.1水污染 Water pollution

是指水体因某种物质的介入，而导致其化学、物理、生物或者放射性等方面特征的改变，从而影响水的有效利用，危害人体健康或者破坏生态环境，造成水质恶化的现象。

Water pollution refers to the phenomenon that the chemical, physical, biological or radiological characteristics of a water body are changed due to the intervention of certain substances, thus affecting the effective use of water, endangering human health or destroying the ecological environment, and resulting in the deterioration of water quality.

4.2生活污水 Domestic sewage

是人们在日常生活中使用过的、并被生活废料所污染的水，来自城市居民区、医院生活区、工厂生活区等。

Water used by people in daily life and polluted by domestic waste, from urban residential areas, hospital living areas, factory living areas, etc.

4.3污水 Sewage

指在生产与生活活动中排放的含有一种或多种污染物的水的总称。

A general term for water containing one or more pollutants discharged in production and domestic activities.

4.4废水处理设备 Sewage treatment equipment

是指可以改善污水水质特征的设备，例如中和调节池，油水分离器，生活用水处理设备（如化粪池、隔油池）等。

Refers to the equipment that can improve the quality characteristics of sewage water, such as neutralization tank, oil-water separator, domestic water treatment equipment (such as septic tank, grease trap).

4.5污水排放口 Sewage outfall

是将污水向水体排放的构筑物。

A structure that discharges sewage into a body of water.

4.6排污许可 Discharge permit

是指环境保护主管部门根据排污单位的申请和承诺，为依法规范和限制排污单位的排污行为，通过发放排污许可证法律文书的形式，明确环境管理要求，对排污单位实施监管执法的环境管理制度。

It refers to an environmental management system whereby the competent department of environmental protection, on the basis of the application and commitment of the pollutant discharging unit, defines the requirements for environmental management and implements supervision and law enforcement over the pollutant discharging unit in order to regulate and limit the discharge behavior of the pollutant discharging unit in accordance with the law by issuing legal documents for discharge permits.

4.7CMA认证 CMA certification

中国计量认证简称。取得实验室资质认定（计量认证）合格证书的检测机构，可按证书上所批准列明的项目，在检测证书及报告上使用CMA标志。

China Metrology Certification for short. The testing institution that has obtained the laboratory qualification identification (metrology certification) certificate may use the CMA mark on the testing certificate and report according to the items approved on the certificate.

5 职责 Responsibilities

## 5.1废水设施运营部门 Sewage facility operation department

5.1.1制定废水相关作业的SOP。

Develop Sops for sewage related operations.

5.1.2制定废水处理设施的维护计划并实施。

Develop and implement maintenance plans for sewage treatment facilities.

5.1.3定期对污水管网进行堵塞排查、清理。

Check and clean up the sewage pipe network regularly.

5.1.4负责本上海浦江数据中心范围内的废水处理和排放设备设施的日常运营管理，如化粪池清运等。当发现异常或故障等情况时，第一时间上报EHS管理负责人。

Responsible for the daily operation management of sewage treatment and discharge equipment and facilities within the scope of the local SHANGHAI PUJIANG Data Center, such as septic tank cleaning and transportation. Report to the manager of EHS in the first time when any abnormality or malfunction is found.

5.1.5加强对可能因为意外泄漏而污染环境的设备设施的管理，以防止污染物意外进入雨水管道造成污染，如柴油发电机、危险化学品储存设施、危险废物贮存设施等。

Strengthen the management of equipment and facilities that may pollute the environment due to accidental leakage, so as to prevent pollutants from accidentally entering stormwater pipes and causing pollution, such as diesel generators, hazardous chemical storage facilities, hazardous waste storage facilities, etc.

5.1.6当上海浦江数据中心区域内有环境污染事件发生时，完成事件调查，并采取整改措施。

When an environmental pollution event occurs in the area of SHANGHAI PUJIANG Data Center, complete the incident investigation and take corrective measures.

5.1.7保留废水排放控制单元的维护记录。

Keep the maintenance records of sewage discharge control unit.

## 5.2采购部门 Purchasing department

5.2.1与化粪池清掏公司签订合同完成化粪池进行定期清掏和抽运。

Sign a contract with septic tank cleaning Company to complete the regular cleaning and pumping of septic tanks.

5.2.2与具有环境检测资质的第三方公司签订合同，完成数据中心废水的采样与检测。

Sign a contract with a third-party company with environmental testing qualifications to complete the sampling and testing of data center sewage.

## 5.3 EHS管理负责人 EHS officer

5.3.1 制定、审查并定期更新该程序。

Develop, review and regularly update the procedure.

5.3.2 对相关人员进行废水管理意识培训。

Conduct sewage management awareness training for relevant personnel.

5.3.3 根据环评批复实施监测。

Implement monitoring according to the EIA approval.

5.3.4 建立并更新上海浦江数据中心各类废水排放源清单。

Establish and update the list of various sewage discharge sources of SHANGHAI PUJIANG Data Center.

5.3.5 指导、监督、检查、审核相关成员对本程序的执行情况。

Guide, supervise, inspect and review the implementation of this procedure by relevant members.

5.3.6 制定检测计划，指导上海浦江数据中心实施检测，并保存检测记录。

Formulate test plan, guide SHANGHAI PUJIANG Data Center to implement test, and save test records.

6 程序 Procedures

## 6.1 雨污分流 Separation of rain and sewage

6.1.1上海浦江数据中心排水采用雨、污分流制。上海浦江数据中心产生的废水应经内部污水管道排入市政污水管网。

The drainage system of SHANGHAI PUJIANG Data Center adopts the rain and pollution separation system. The sewage generated by SHANGHAI PUJIANG Data Center shall be discharged into the municipal sewage network through the internal sewage pipe.

6.1.2严禁将生活污水等废水排入至雨水管网中。

It is strictly prohibited to discharge domestic sewage and other sewage into the stormwater network.

## 6.2废水污染源识别Identification of sewage pollution sources

6.2.1上海浦江数据中心的废水排放包括生活污染水与生产废水，生产废水包括浓水排水、反洗排水、清洗冷却塔排水等。

The sewage discharge of SHANGHAI PUJIANG Data Center includes domestic polluted water and production sewage, and the production sewage includes concentrated water drainage, backwash drainage, and cleaning and cooling tower drainage.

6.2.2生活污水：来自上海浦江数据中心办公区域卫生间，经化粪池预处理后排入市政污水管网。

Domestic sewage: It comes from the toilet of the office area of SHANGHAI PUJIANG Data Center and enters the municipal sewage network after pretreatment by the septic tank.

## 6.3 污水处理系统Sewage treatment system

6.3.1如果不同区域数据中心有污水处理设施请参照下列执行，如所在数据中心没有污水处理设施，则无需执行下列要求。

If the data center in different regions has sewage treatment facilities, please refer to the following. If the data center does not have sewage treatment facilities, it is not necessary to perform the following requirements.

6.3.2上海浦江数据中心污水管网设施包括管网、检修口、排放口和污水处理设备等。当排水系统管网发生变化时，上海浦江数据中心需要及时更新图纸。

Sewage pipe network facilities of SHANGHAI PUJIANG Data Center include pipe network, overhaul port, discharge port and sewage treatment equipment, etc. When the drainage system pipe network changes, SHANGHAI PUJIANG Data Center needs to update the drawings in time.

6.3.3废水处理设备：生活污水以及其他污水进入市政管网前的主要废水处理设备为化粪池。

Sewage treatment equipment: The main sewage treatment equipment for domestic sewage and other sewage before entering the municipal pipe network is septic tank.

6.3.4与现有废水处理设备相关的新改扩建或拆除工程，需在工作启动之初（可行性研究或初步设计阶段）判断是否需要进行环境影响评价（需询问属地生态环境局是否需要）等前置工作，并确保计划执行过程的合规性。

For new renovation, expansion or demolition projects related to existing sewage treatment equipment, it is necessary to determine at the beginning of the work (feasibility study or preliminary design stage) whether it is necessary to carry out environmental impact assessment (it is necessary to ask the local ecological environment bureau whether it is necessary) and other preliminary work, and ensure the compliance of the plan implementation process.

## 6.4 污水处理系统的日常维护

6.4.1 EHS管理负责人对上海浦江数据中心水管网进行定期检查，并建立检查表、保存检查记录。检查项目主要包括但不限于：排污口标识是否完好、检查井是否堵塞、检查井接口处是否有渗漏、污水排水管道是否有堵塞等。

The person in charge of EHS management shall carry out regular inspection of the water pipe network of SHANGHAI PUJIANG Data Center, establish inspection list and keep inspection records. The inspection items mainly include but are not limited to whether the sewage outlet mark is in good condition, check whether the well is blocked, check whether there is leakage at the well interface, and check whether the sewage drainage pipe is blocked, etc.

6.4.2负责委托化粪池清掏公司对化粪池进行定期清掏和抽运，并明确污水的最终去向。

Be responsible for entrusting the septic tank cleaning company to carry out regular cleaning and pumping of the septic tank and determine the final destination of the sewage.

6.4.3汛期到来之前，上海浦江数据中心应根据各区域的实际情况采取必要的清淤清堵等措施，疏通雨水排水系统，避免过量雨水流入污水系统。

Before the flood season, SHANGHAI PUJIANG Data Center shall take necessary measures such as dredging and blocking according to the actual situation of each region to dredge the rainwater drainage system and avoid excessive rainwater flowing into the sewage system.

6.4.4所有受影响成员应参加废水管理相关培训，合规排放生活污水，禁止将生活污水等废水排入雨水管网，禁止将化学药剂排入污水管网与雨水管网。

All affected members shall participate in relevant training on sewage management, discharge domestic sewage in compliance, and prohibit the discharge of domestic sewage and other sewage into the stormwater pipe network, and prohibit the discharge of chemical agents into the sewage pipe network and stormwater pipe network.

6.4.5上海浦江数据中心内任何人员发现排水系统有堵塞或不通畅等情况时，应第一时间向EHS管理负责人报告。

If any personnel in SHANGHAI PUJIANG Data Center finds the drainage system blocked or not unobstructed, they shall immediately report to the EHS officer in charge.

6.4.6为减少水污染物排放，上海浦江数据中心各所属区域的盥洗间、卫生间等产生生活污水的区域，张贴节约用水宣传、告知标志。

In order to reduce the discharge of water pollutants, the washrooms, toilets and other areas where domestic sewage is generated in each area of SHANGHAI PUJIANG Data Center shall be posted with water conservation publicity and notification signs.

## 6.5 排污口规范化管理 Standardized management of sewage discharge outlets

6.5.1根据相关法规要求，污水排放口应设置专用标识并统一按照规范标准编号。

According to the requirements of relevant laws and regulations, the sewage discharge outlet should be set up special signs and numbered in accordance with the standard.

6.5.2 EHS管理负责人应确保排污口的标识牌的样式和内容符合法规要求，并定期巡查，保持清晰完整。标识牌具体要求按照《环境保护图形标志》排放口及《关于印发排放口标志牌技术规格的通知》要求设置。一般性污染物监测点位设置提示性标志牌。排放剧毒、致癌物及对人体有严重危害物质的监测点位设置警告性标志牌，警告标志图案应设置于警告性标志牌的下方，详情参考附件1。

The person in charge of EHS management shall ensure that the pattern and content of the sign plate at the sewage discharge outlet meet the requirements of laws and regulations, and conduct regular inspection to keep it clear and complete. The specific requirements of the sign plate shall be set in accordance with the requirements of the "Environmental Protection Graphic Sign" discharge port and the "Notice on printing and distributing Technical Specifications of the discharge port sign Plate". General pollutant monitoring points shall be set up suggestive signs. Warning signs shall be set at monitoring points for discharge of highly toxic, carcinogenic substances and substances that are seriously harmful to the human body, and the warning sign pattern shall be set below the warning sign, for details, refer to Attachment 1.

6.5.3 EHS管理负责人需建立上海浦江数据中心污水排放口及污水监测点位台账及位置图。

The EHS officer shall establish the log and location map of sewage discharge outlet and sewage monitoring point of SHANGHAI PUJIANG Data Center.

## 6.6 水污染物监测 Water pollutant monitoring

6.6.1委托检测：根据排污许可证或者排污登记（如数据中心开展了环境影响评价并取得批复，或者最新排污许可相关法规要求，污水监测则执行相关规定。）规定要求频次定期委托具有环境检测资质的第三方公司，对废水进行采样与检测, 检测频次不低于 1 次/年。污水排放执行标准应根据《污水综合排放标准》（GB 8978）中表4“三级标准”，上海市污水综合排放标准（DB31/199-2018）中表2“三级标准”中的相关限值，具体限值如下表1：

Commissioned testing: According to the discharge permit or discharge registration (if the data center has carried out environmental impact assessment and obtained the approval, or the latest discharge permit related regulations, sewage monitoring shall implement the relevant provisions.) The regulations require the frequency of regularly commissioning a third-party company with environmental testing qualifications to sample and test the sewage, and the detection frequency is not less than once/year. The implementation standard of sewage discharge should be based on the relevant limits in Table 4 "three-level standard" in the "Comprehensive Sewage Discharge Standard" (GB 8978), the specific limits are as follows:

表1污水排放限值

Table 1 Limits of sewage discharge

| 检测指标 Indicator | 排放限值 Limit | 单位 Unit | 监测点位 Monitoring position |
| --- | --- | --- | --- |
| pH值 | 6~9（华东） 6.5~9 （华北） | - | 单位废水总排口 Main wastewater outlet |
| 化学需氧量CODcr | 500 | mg/L |  |
| 五日生化需氧量BOD5 | 300 | mg/L |  |
| 氨氮 NH3-N | 45 | mg/L |  |
| 悬浮物 SS | 400 | mg/L |  |
| 溶解性总固体 TDS | 2000（华东） 1600（华北） | mg/L |  |
| 总氮 TN | 70 | mg/L |  |
| 总磷TP | 8 | mg/L |  |

6.6.2监督检测：由生态环境主管部门或代表执法部门的第三方检测机构，按照法规的要求定期对上海浦江数据中心废水进行的采样和检测。

Supervision and testing: The competent department of ecological environment or the third-party testing institution representing the law enforcement department shall regularly sample and test the sewage of SHANGHAI PUJIANG Data Center in accordance with the requirements of laws and regulations.

6.6.3验收检测：当上海浦江数据中心新建、改建或扩建项目竣工后，在项目投产和运行前，需要对建设项目环境保护设备进行验收检测。

Acceptance test: After the completion of the new construction, reconstruction or expansion project of SHANGHAI PUJIANG Data Center, acceptance test shall be carried out on the environmental protection equipment of the construction project before the project is put into operation.

6.6.4应急检测：当上海浦江数据中心内发生了某些足以影响到废水水质变化的事故或者事件，为了及时准确地评估废水排放的合规性而进行的应急采样和检测。

Emergency testing: When some accidents or events occur in SHANGHAI PUJIANG Data Center that can affect the change of sewage quality, emergency sampling and testing shall be carried out in order to timely and accurately evaluate the compliance of sewage discharge.

6.6.5检测计划：EHS管理负责人负责按照相关法规要求，制定年度委托检测计划，并及时更新。

Test plan: the EHS officer shall be responsible for formulating the annual commissioned test plan according to the requirements of relevant laws and regulations and update it in time.

6.6.6检测报告和记录：上海浦江数据中心需负责保存原始检测报告。

Test report and record: SHANGHAI PUJIANG Data Center shall be responsible for saving the original test report.

6.6.7检测单位资质要求：委托的第三方监测单位应具有“检验检测机构资质认定证书”，可出具带有“CMA”标志的检测报告，其资质认定证书范围内须包括环境类水质指标检测项目。

Qualification Requirements of the testing unit: The entrusted third-party monitoring unit shall have the "Qualification Certificate of Inspection and Testing Organization" and can issue the test report with the "CMA" mark. The scope of the qualification certificate shall include the environmental water quality index test items.

## 6.7 废水排放应急预案 Emergency plan

6.7.1上海浦江数据中心应制定《突发环境事件应急预案》，以指导相关各方的应急准备、响应及沟通、汇报等工作。

SHANGHAI PUJIANG Data Center shall formulate Emergency Plan for Environmental Emergencies to guide relevant parties' emergency preparation, response, communication and reporting.

6.7.2水污染物超标响应要点Key points of response to excessive water pollutants:

- 停止对应排口向市政污水管网排水。上海浦江数据中心人员共同排查该排放口覆盖的排水区域，以确认超标排放的源头。

Stop the corresponding outlet to discharge water to the municipal sewage network. SHANGHAI PUJIANG Data Center personnel jointly check the drainage area covered by the discharge port to confirm the source of excessive discharge.

- 对超标原因进行分析，并采取措施消除超标原因。

Analyze the causes of excessive discharge and take measures to eliminate the causes of excessive discharge.

- 超标原因消除后，再次由第三方检测单位采样，检测合格后方可恢复排水。

After the cause of exceeding the standard is eliminated, the sample is again collected by a third-party testing unit, and the drainage can be resumed after the test is qualified.

6.7.3 化学品意外泄漏进入污水管网的应急响应和预防要点Key points for emergency response and prevention of accidental leakage of chemicals into the sewage pipe network:

- 为防止化学品的意外泄漏，各受影响部门需要加强对各自化学品储存及使用区域的日常巡视，确保容器的有效性和正常使用，以消除化学品意外泄漏对污（雨）水排水系统的污染风险。

In order to prevent accidental leakage of chemicals, the affected departments need to strengthen the daily inspection of their own chemical storage and use areas to ensure the effectiveness and normal use of containers, so as to eliminate the risk of pollution of accidental leakage of chemicals to the sewage (rain) water drainage system.

- 上海浦江数据中心需在化学品的存储和使用地点配备适用的化学品泄漏应急装备及合适PPE等物资。

SHANGHAI PUJIANG Data Center shall be equipped with appropriate chemical leakage emergency equipment, appropriate PPE and other materials at the storage and use places of chemicals.

- 液体化学品（如冷冻液、润滑油、水处理药剂等桶装化学品）泄漏时，发现人员应第一时间向数据中心EHS管理负责人报告。同时，尽快通知应急受训人员到场采取处置措施。当泄漏点周边有可能受影响的污（雨）水排放口或者检查井时，需使用沙袋对排口或检查井进行围堵，防止泄漏物流入污（雨）水管网。

When liquid chemicals (such as refrigerant, lubricating oil, water treatment chemicals, etc.) leak, the personnel should immediately report to the data center EHS officer. At the same time, inform the emergency trained personnel to take disposal measures on site as soon as possible. When there are sewage (rain) water discharge outlets or inspection Wells that may be affected around the leakage point, sandbags should be used to block the discharge outlets or inspection Wells to prevent leakage into the sewage (rain) water pipe network.

- 柴油发电机储油罐发生泄漏时，需要根据《突发环境事件应急预案》及其现场处置预案实施泄漏后的应急反应操作程序，降低环境影响。

When the oil storage tank of diesel generator leaks, it is necessary to implement the emergency response operation procedures after the leak according to the Emergency Plan for Environmental Emergencies and its on-site disposal plan to reduce the environmental impact.

## 6.8审核与审查 Audit and review

6.8.1 EHS管理负责人应至少每年对废水管理执行情况进行一次合规性审计，并提出纠正和预防措施。

The EHS Management leader shall conduct a compliance audit of sewage management implementation at least once a year and propose corrective and preventive actions.

6.8.2 EHS管理负责人应至少每年对本程序进行一次审查。

The EHS Management Leader shall conduct a review of this procedure at least annually.

## 6.9文件管理 File management

6.9.1 EHS管理负责人负责建立公司污水排放口及监测点位台账，每年回顾并保持及时更新。

The EHS officer shall be responsible for establishing the company's sewage discharge outlet and monitoring point log, review it annually and keep it updated in time.

6.9.2 EHS管理负责人应保存废水的检测报告，保存期限不少于5年。

The EHS officer shall keep the test report of sewage for at least 5 years.

6.9.3 EHS管理负责人负责维护上海浦江数据中心污水排放系统检查、维修记录，所有记录保存期限不少于5年。

The EHS officer shall be responsible for maintaining the inspection and maintenance records of the sewage discharge system of SHANGHAI PUJIANG Data Center, and the retention period of all records shall not be less than 5 years.

6.9.4 EHS管理负责人负责成员在岗培训，培训记录保存期限不少于5年。

The person in charge of EHS management shall be responsible for on-job training of members, and the retention period of training records shall not be less than 5 years.

7附件 Attachments

- IF-PJ-EHS-2801 废水排放源清单 Sewage Source List

- IF-PJ-EHS-2802废水排放口与监测点位环境图形标志牌设置要求（示例） Requirements for setting of graphic signs for Sewage discharge outlets and monitoring points (Example)

废水排放口与监测点位环境图形标志牌设置要求（示例）

Requirements for setting of graphic signs for sewage discharge outlets and monitoring points (Example)

| 项目 Item | 示例 Example | 标志牌要求 Requirements |
| --- | --- | --- |
| 废水排放口 Outlet | 提示标志 Signs： 警告标志Signs： | 1、尺寸要求 （1）平面固定式标志牌外形尺寸 ①提示标志：480×300mm ②警告标志：边长420mm （2）立式固定式标志牌外形尺寸 ①提示标志：420×420mm ②警告标志：边长560mm ③高度：标志牌最上端距地面2m 地下0.3m 1. Size requirements (1) Flat fixed sign appearance size ① Prompt sign: 480×300mm ② Warning sign: side length 420mm (2) Vertical fixed sign outline size ① Prompt sign: 420×420mm ② Warning sign: side length 560mm ③ Height: the top end of the sign is 0.3m from the ground 2m underground |
| 废水监测点位 Monitoring points | 提示性污水监测点位标志牌Indicator Sign for Sewage Monitoring Point： | 1、监测测点位标志牌尺寸要求： ①尺寸要求：边框600mm× 500mm； ②二维码：100mm×100mm 2、监测点位标志牌信息内容： 单位名称、点位编码、污水来源、净化工艺、排放去向及污染物种类。 1, monitoring point sign size requirements: ① Size requirements: frame 600mm×500mm. ② Two-dimensional code: 100mm×100mm 2, monitoring point sign information content: Unit name, point code, sewage source, purification process, discharge direction and pollutant type. |