变配电站安全管理制度

Substation Safety Management System

内部使用

在使用前，请和文档编写人员确认本文档为最新版本。

未经上海暻熠数据科技有限公司、上海暻耀网络技术有限公司书面许可，其它任何机构或个人不可传阅、引用或复制本文件的内容。

Internal use

Before using, check with the documentation writer to make sure this document is the latest version.

Without the written permission of Shanghai Jingyi Data Technology Co., Ltd., Shanghai Jingyao internet Technology Co., Ltd., no other organization or individual is allowed to circulate, quote or copy the content of this document.

| 文件编号Documents | IP-PJ-EHS-07 |
| --- | --- |
| 版 本Edition | V1.0 |
| 文件维护部门File maintenance department | 上海浦江数据中心 |
| 会签部门Document Signing department | 上海浦江数据中心 |
| 执行范围Scope of execution | 上海浦江数据中心 |

文件修订记录

Document revision record

| 版本号 Edition | 版本日期 Date | 修订内容 Revised Content | 修订人员 Revision personnel | 核准员 Approver | 备注 Remarks |
| --- | --- | --- | --- | --- | --- |
| V1.0 | 2025-06-25 | 初版发布 | 楚靖岳 | 陆磊 |  |

目录 Content

1 目的Purpose	4

2 适用范围Scope of application	4

3 规范性引用文件Reference documents	4

4 术语和定义Terms and definitions	5

5 职责Responsibility	5

5.1 变配电站运行人员Substation operation personnel	5

5.2 EHS管理负责人EHS officer	6

5.3 变配电站主管负责人Substation officer	6

6 程序Procedures	7

6.1 一般要求General requirements	7

6.2 值班与交接班Duty and shift handover	9

6.3 巡视检查Inspection and patrol	11

6.4 设备验收 Equipment acceptance	13

6.5 设备缺陷管理Equipment defect management	14

6.6工作票、操作票Work permits and operation tickets	14

6.7 倒闸操作Switching operations	16

6.8 设备预防性试验Equipment preventive testing	18

6.9 运行维护 Operation maintenance	19

6.10 安保、环境管理Security and environmental management	20

6.11 安全工器具管理Safety tool management	22

6.12 消防管理Fire safety management	23

6.13 安全标志标示配置和使用管理Safety signage configuration and usage management	24

7 附件Attachments	25

1 目的Purpose

为了加强变配电站安全管理、规范变配电站的运行、以及电气设备、设施的操作与维护，保持变配电站的长期、安全、稳定运行，防范电气安全事故，特制定本运行规程。

To strengthen substation safety management, standardize the operation of substations, and regulate the operation and maintenance of electrical equipment and facilities, ensuring the long-term, safe, and stable operation of substations while preventing electrical accidents, this operating procedure is formulated.

2 适用范围Scope of application

适用于上海浦江数据中心变配电站（包括110KV及以下）的安全管理。

Applicable to the safety management of substations (including 110kV and below) in SHANGHAI PUJIANG Data Center.

3 规范性引用文件Reference documents

GB 2894  安全标志及其使用导则

GB 2894 Safety Signs and Guidelines for Use

GB 26860  电力安全工作规程 发电厂和变配电站电气部分

GB 26860 Safety Code for Electric Power Industry-Electrical Parts of Power Plants and Substations

GB 50053  20kV 及以下变电所设计规范

GB 50053 Design Code for 20kV and Below Substations

GB 50054  低压配电设计规范

GB 50054 Design Code for Low-Voltage Electrical Installations

GB 50059  35～110kV 变电所设计规范

GB 50059 Design Code for 35～110kV Substations

GB 50060  3～110kV 高压配电装置设计规范

GB 50060 Design Code for High-Voltage Electrical Installations (3～110kV)

GB 50140  建筑灭火器配置设计规范

GB 50140 Code for Design of Fire Extinguisher Distribution in Buildings

GB 50150  电气装置安装工程 电气设备交接试验标准

GB 50150 Standard for Handover Testing of Electrical Equipment in Electrical Installation Engineering

GB 50444  建筑灭火器配置验收及检查规范

GB 50444 Code for Acceptance and Inspection of Fire Extinguisher Distribution in Buildings

GB/T 31143  电弧故障保护电器（AFDD）的一般要求

GB/T 31143 General Requirements for Arc Fault Detection Devices (AFDD)

GB/T 24274  低压抽出式成套开关设备和控制设备

GB/T 24274 Low-Voltage Withdrawable Switchgear and Control gear Assemblies

GB/T 32893  10kV 及以上电力用户变电站运行管理规范

GB/T 32893 Operational Management Specification for 10kV and Above Power User Substations

GB/T 29639  生产经营单位生产安全事故应急预案编制导则

GB/T 29639 Guidelines for the Preparation of Emergency Response Plans for Production Safety Accidents in Enterprises

4 术语和定义Terms and definitions

4.1高压High voltage

交流电力系统中超过1000V的电压等级，直流电力系统中超过1500V的电压等级。

In AC power systems, voltage levels exceeding 1000V. In DC power systems, voltage levels exceeding 1500V.

4.2倒闸操作Switching operation

电气设备分为运行、备用、检修三种状态。将设备由一种状态转变为另一种状态的过程叫倒闸，所进行的操作叫倒闸操作。

Electrical equipment operates in three states: running, standby, and maintenance. The process of transitioning equipment from one state to another is called switching, and the corresponding operations are referred to as switching operations.

5 职责Responsibility

## 5.1 变配电站运行人员Substation operation personnel

5.1.1 对变配电站设备负有运行、监视和维护责任，认真贯彻执行各项规章制度和有关运行工作的各项规定。

Responsible for the operation, monitoring, and maintenance of substation equipment, strictly implementing all regulations and operational guidelines.

5.1.2 严格执行电网调度命令，认真执行二票三制度：工作票、操作票、交接班制度、巡回检查制度、设备定期试验轮换制度。

Must strictly comply with power grid dispatch commands and rigorously enforce the "Two Tickets & Three Systems": work permit, operation ticket, shift handover system, patrol inspection system, equipment periodic testing and rotation system.

5.1.3 熟悉变配电站一、二次接线，了解有关系统运行方式，掌握正确操作及维护方法，正确处理事故及异常运行情况。

Must be familiar with primary and secondary wiring of the substation, understand relevant system operation modes, master correct operation and maintenance methods, and properly handle accidents and abnormal operating conditions.

5.1.4 负责做好现场安全措施，保证检修人员的工作安全。

Responsible for implementing on-site safety measures to ensure the safety of maintenance personnel.

5.1.5 按规定做好各种记录。

Must maintain various records as required.

5.1.6 对安全工具、消防设备、事故备品定期检查，保证完好齐全。

Conduct regular inspections of safety tools, firefighting equipment, and emergency spare parts to ensure they are complete and in good condition.

5.1.7 搞好站内文明生产工作，保持设备环境清洁，防止小动物和雨水进入变配电站。

Maintain orderly production within the station, keep equipment and the environment clean, and prevent small animals and rainwater from entering the substation.

5.1.8 禁止无关人员进入变配电站，对有关人员出入进行登记。

Unauthorized personnel are prohibited from entering the substation, and access by authorized personnel must be registered.

## 5.2 EHS管理负责人EHS officer

5.2.1 学习本制度及国家级电力部门有关电气安全的标准规范。

Study this regulation and relevant national electrical safety standards and specifications issued by power authorities.

5.2.2 监督变电站运维人员落实本制度。

Supervise substation operation and maintenance personnel in implementing this regulation.

5.2.3 经常性的对变配电站进行安全检查。

Conduct regular safety inspections of substations.

5.2.4 在发现变配电站运行不正常、或人员的违规操作时立即向变配电站主管人员汇报并制止违章行为。

Immediately report to substation management and stop any non-compliant operations upon discovering abnormal substation conditions or personnel violations.

## 5.3 变配电站主管负责人Substation officer

5.3.1 确保变配电站安全生产岗位责任制、各项运行管理制度以及本制度得到落实。

Ensure the implementation of the substation safety production responsibility system, all operational management regulations, and this management system.

5.3.2 组织变配电站学习各项变电站安全运行的法律、法规、标准、规范以及公司的规章制度。

Organize training for substation personnel on laws, regulations, standards, and company policies related to substation safety operations.

5.3.3 对变配电站的运维作业进行经常性的督导检查及隐患排查，及时处理发现的问题。

Conduct regular supervision, inspection, and hazard identification for substation operation and maintenance activities, and promptly address any identified issues.

5.3.4 按公司违规、违纪制度，严肃处理运维人员的违规行为。

Strictly penalize violations by operation and maintenance personnel in accordance with the company's disciplinary policies.

5.3.5 组织运维人员按照应急预案的要求定期进行变电站安全事故的应急演练，记录演练过程并总结演练效果。

Organize regular emergency drills for substation safety incidents as required by emergency response plans, document the drill process, and evaluate the outcomes.

6 程序Procedures

## 6.1 一般要求General requirements

6.1.1变/配电站应建立、健全变配电站安全生产岗位责任制、各项运行管理制度和安全操作规程，主要内容应上墙明示，变/配电站的以下制度必须严格遵守：

Substations/power distribution stations shall establish and improve the safety production responsibility system, operational management regulations, and safety operating procedures. Key contents shall be prominently displayed on-site. The following regulations must be strictly adhered to:

- 值班制度Duty shift system

- 交接班制度Shift handover system

- 巡视检查制度Inspection and patrol system

- 设备验收制度Equipment acceptance system

- 设备缺陷管理制度Equipment defect management system

- 工作票、操作票管理制度Work permit and operation ticket management system

- 倒闸操作管理制度Switching operation management system

- 设备预防性试验制度Equipment preventive testing system

- 设备运行维护管理制度Equipment operation and maintenance management system

- 场地环境管理制度Site environmental management system

- 应急预案管理制度Emergency response plan management system

6.1.2 变/配电站的各种记录档案应分类归档，设计、施工、竣工验收的图纸、图表等文件资料长期保存，其他记录至少保存1年。

All records and archives of substations/power distribution stations shall be categorized and filed. Design, construction, and completion acceptance drawings, charts, and other documents shall be stored long-term, while other records shall be retained for at least one year.

6.1.3 变/配电站应建立设备异常、停电、触电、汛害、电气设备火灾爆炸等情况的应急预案，且在现场备存。

Substations/power distribution stations shall establish emergency response plans for equipment abnormalities, power outages, electric shocks, flood damage, electrical fires, explosions, etc., and keep them on-site.

6.1.4 变配电站应急预案演练每年不少于2次，演练结束后应分析演练中的问题，对演练效果进行评估，撰写演练总结报告。

Emergency drills shall be conducted at least twice a year. Post-drill analysis shall identify issues, evaluate effectiveness, and summarize findings in a report.

6.1.5 变配电站空气温度应位于摄氏5℃-40℃之间，相对湿度40%-60%，设备区域内应配有温、湿度计。

The ambient temperature in substations shall be maintained between 5°C and 40°C, with relative humidity at 40%-60%. Temperature and humidity gauges shall be installed in equipment areas.

6.1.6室内变压器、高压配电装置、低压配电装置的操作区、维护通道应铺设绝缘胶垫。

Insulated rubber mats shall be laid in indoor transformer areas, high/low-voltage distribution operation zones, and maintenance walkways.

6.1.7 电缆沟盖板齐全，电缆夹层、电缆沟和电缆室设置的防水、排水措施完好有。

Cable trench covers shall be complete, with functional waterproofing and drainage measures in cable mezzanines, trenches, and rooms.

6.1.8 设备构架、基础无严重腐蚀，房屋不漏雨，无未封堵的孔洞、沟道。

Equipment structures and foundations shall show no severe corrosion. Buildings shall be leak-free, with no unsealed holes or ducts.

6.1.9 正常照明和应急照明系统应完好,疏散指示标志灯的持续照明时间应大于30min。

Normal and emergency lighting systems shall be fully operational. Emergency exit signs shall maintain illumination for >30 minutes.

6.1.10 对装有产生有毒气体、窒息性气体的配电装置的房间，在发生事故时房间内易聚集气体的部位，应装设强制向外排风装置。

Rooms housing equipment producing toxic/asphyxiating gases shall have forced exhaust ventilation installed at gas accumulation points for accident scenarios.

6.1.11 室内变配电装置布置、安全净距、通道与围栏等应符合 GB 50053、GB 50054、GB 50059、GB50060 等的要求。

Indoor equipment layout, safety clearances, walkways, and enclosures shall comply with GB 50053, GB 50054, GB 50059, and GB 50060 standards.

6.1.12 长度大于7米的变/变配电站应设置两个安全出口，并宜布置在变/变配电站的两端，变压器室、变配电站、电容器室的门应向外开启，变/变配电站出入口应设置高度不低于400mm 的防小动物挡板并采取其他防鼠措施。

Substations >7m in length shall have two emergency exits preferably at opposite ends. Transformer/power distribution/capacitor room doors shall open outward. Entrances shall have ≥400mm anti-vermin barriers with additional rodent prevention measures.

6.1.13 变配电站内环境整洁，场地平整，设备间不应存放与运行无关的物品，不应有与其无关的管道和线路通过，巡视道路应畅通。

Substation environments shall be clean and level. Equipment rooms shall not store non-operational items or host unrelated pipelines/cabling. Inspection routes shall remain unobstructed.

6.1.14 当变配电站设置在地下时，应采取防水措施。

Underground substations shall implement waterproofing measures.

6.1.15 应设置符合GB 50140要求的适用电气火灾的消防设施、器材，并定期维护、检查和测试。现场消防设施、器材不应挪作他用，周围不应堆放杂物和其他设备。

Firefighting equipment compliant with GB 50140 for electrical fires shall be installed, regularly maintained, inspected, and tested. On-site firefighting equipment shall not be repurposed, with clear surrounding areas.

6.1.16 变配电站应保持进出畅通，不应堵塞或占用，室内严禁烟火，对明火作业应办理审批手续，严加管理。

Substation access routes shall remain unobstructed. Open flames are prohibited indoors, with strict approval procedures for hot work.

6.1.17 变配电站内非消防负荷配电回路应安装电气火灾监控系统，其二级、三级配电回路安装有电气火灾监控系统的，应接入到变配电站内电气火灾监控系统，电气火灾监控系统应具备良好的上下级数据接口兼容性。

Non-firefighting load circuits shall install electrical fire monitoring systems. Secondary/tertiary distribution circuits with such systems shall integrate with the substation's monitoring network, ensuring cross-level data compatibility.

## 6.2 值班与交接班Duty and shift handover

6.2.1 值班人员应取得合格有效的电工作业操作资格证书，资格证书原件由值班人员上岗时随身携带或由单位统一进行管理。

On-duty personnel must possess valid and qualified electrician operation certificates. The original certificate shall be carried during duty or managed by the organization.

6.2.2 值班人员应掌握与其工种、岗位有关的电气设备的性能及操作方法，熟悉各种消防设备的性能、布置、适用范围和使用方法，熟悉应急预案内容和处置流程，掌握触电急救和心肺复苏方法。

On-duty personnel should be proficient in the performance and operation methods of electrical equipment related to their specific trades and positions. They must be familiar with the functions, layout, applicable scope, and usage procedures of various firefighting equipment, as well as the content and response procedures of emergency plans. Additionally, they should master first aid techniques for electric shock and cardiopulmonary resuscitation (CPR).

6.2.3 值班人员的配置应符合下列要求：

Staffing requirements for on-duty personnel shall comply with the following:

a) 有人值班变配电站：35kV电压等级的变配电站，10/6kV 电压等级且变压器容量在 630kVA及以上的变配电站，应安排专人值班，每班值班人员不少于2人，且应明确其中1人为值长。

Manned substations: substations with a voltage level of 35kV. Substations with a voltage level of 10/6kV and a transformer capacity of 630kVA or above. These substations shall be staffed with dedicated on-duty personnel, with no fewer than two operators per shift, one of whom shall be clearly designated as the shift supervisor.

b) 无人值班变配电站：采用智能化运维模式的变配电站可不设专人值班，负责其运管理的智能运维中心应安排全天24小时专人值班，每班值班人员不少于2人，且应明确其中1人为值长，并应按所管理的变配电。站数量、设备规模和用电负荷的级别等配置智能运维操作队的人员；10/6kV 电压等级且变压器容量在500kVA及以下的变配电站，可不设专人值班，但应由电工人员负责运行检查工作。

Unattended substations: substations using intelligent operation and maintenance mode, on-site dedicated staff is not required. However, the intelligent operation and maintenance center in charge should have dedicated staff on duty 24/7. Each shift should have at least two staff, with one designated as the shift leader. The number of staff in the intelligent operation and maintenance team should be configured according to the number of managed substations and distribution stations, equipment scale, and electrical load level. For those with a voltage level of 10/6kV and a transformer capacity of 500kVA or less, on-site dedicated staff is not necessary, but electricians should conduct operation inspections.

6.2.4 值班人员上岗期间应穿全棉长袖工作服和绝缘鞋。

Duty personnel shall wear full-cotton long-sleeved work clothes and insulated shoes during their shift.

6.2.5无论高压设备是否带电，工作人员不得单独移开或越过遮栏进行工作；若有必要移开遮栏时，应有监护人在场并保持与高压设备的安全距离。

Regardless of whether high-voltage equipment is energized, workers shall not remove or bypass protective barriers alone. If barrier removal is necessary, a supervisor must be present while maintaining safe distance from high-voltage equipment.

6.2.6 当班时，值班人员应坚守工作岗位，不得从事工作无关的活动。换班时必须认真履行交接班制度，做好交接班记录，非变配电站值班人员因工作需要进入变配电站设备区时应登记，值班人员应监护陪同。

During duty hours, personnel shall remain at their workstations and refrain from non-work-related activities. Shift changes must strictly follow handover procedures with proper documentation. Non-duty personnel entering substation equipment areas for work purposes must register and be accompanied by duty personnel.

6.2.7 交接班前，接班人员应认真阅读运行日志，并按设备巡视路线图巡查一、二次设备，试验中央信号装置等交接项目，对严重缺陷、设备变更或有疑问应进行现场交接。

Before shift handover, the relieving personnel should carefully read the operation log, inspect primary and secondary equipment along the equipment patrol route map, and test handover items like the central signal device. For serious defects, equipment changes or matters in doubt, on-site handover is required.

6.2.8 接班人员应认真听取交接内容，核对模拟图和现场运行方式，交接完毕双方签名。

The relieving personnel should listen attentively to the handover content, verify the mimic diagram and on-site operation mode, and both parties should sign after the handover is completed.

6.2.9 在处理事故或进行倒闸操作时，不得进行交接班；交接班中如遇事故，须停止交接，接班人员可在交班人员指挥下协助处理事故。

During accident handling or switching operations, shift handover is prohibited. If an accident occurs during handover, the handover must be stopped, and the relieving personnel can assist in handling the accident under the outgoing personnel's command.

6.2.10 如遇接班人员醉酒、精神失常等情况，应拒绝交接，并立即汇报领导。

In case the relieving personnel are drunk or mentally abnormal, the handover should be refused, and the superior should be reported immediately.

6.2.11 遇有接班者未能准时到班，交班者应坚守岗位并汇报领导。

If the relieving personnel fail to arrive on time, the outgoing personnel should stay at their posts and report to the superior.

## 6.3 巡视检查Inspection and patrol

6.3.1 有人值班的变配电站每班应至少巡视检查1次。

Manned substations shall conduct at least one inspection per shift.

6.3.2 无人值班的变配电站应根据电气运行环境、电气设备运行工况、负载等具体情况安排巡视检查，每周至少1次。

Unmanned substations shall arrange inspections based on specific conditions including electrical operating environment, equipment status, and load conditions, with a minimum frequency of once per week.

6.3.3变配电所主管负责人、主管技术人员应经常进行监督性巡视检查和夜间巡视, 并做好记录。

The responsible supervisor and technical personnel of the substation shall regularly perform supervisory inspections and night patrols and maintain proper records.

6.3.4 下列项目应列入巡视检查内容：

The following items shall be included in the inspection checklist:

- 整体运行情况检查：确认设备工作状态正常，电气运行环境正常，观察面板仪表及信号信息正常，无异常声响，无异常气味，操作电源无异常等；

Overall operation inspection: confirm that the equipment is in normal working condition, the electrical operation environment is normal, the panel instruments and signal information are normal, there is no abnormal noise or odor, and the operating power supply is normal, etc.

- 设备外观检查：确认连接点无过热无变色，绝缘无裂纹和明显老化，运行温度无异常，无闪络放电痕迹，操作机构无异常等。

Equipment appearance inspection: confirm that there is no overheating or discoloration at the connection points, no cracks or obvious aging in the insulation, normal operating temperature, no flashover and discharge marks, and no abnormalities in the operating mechanism, etc.

- 运行中的一、二次设备，直流设备；处于备用状态的设备；电气照明及通风设备；消 防设备；电缆沟、构架及房屋；防雷保护及接地装置等应列入巡查内容。

Primary and secondary equipment, DC equipment in operation, equipment in standby state, electrical lighting and ventilation equipment, fire protection equipment, cable trenches, structures and buildings, lightning protection and grounding devices, etc. should be included in the inspection scope.

6.3.5 出现以下情况应增加巡视次数：

The number of inspections should be increased in the following situations:

- 新装或长期停用设备、大修后设备、事故处理后的设备；

Newly installed equipment, equipment that has been out of service for a long time, equipment after major overhauls, and equipment after accident handling.

- 发现运行参数异常等可疑现象或已有缺陷的设备；

Equipment with suspicious phenomena such as abnormal operating parameters or existing defects.

- 变压器满负荷、过负荷或负荷有显著增加时；

When the transformer is at full load, overload, or the load increases significantly.

- 在大风、暴雨、雷电天气。

During strong wind, heavy rain, and thunderstorm weather.

6.3.6 值班人员检查设备时，应严格遵守《电业安全工作规程》和变配电所现场运行规程，在保证安全的前提下，根据各类设备的检查项目，逐一仔细核查，并认真记录。

When inspecting equipment, on-duty personnel shall strictly comply with the "Electrical Safety Work Regulations" and the on-site operation procedures of the substation. Under the premise of ensuring safety, they shall carefully check each item according to the inspection requirements of various equipment and make detailed records.

6.3.7 巡视高压设备的人员巡视高压设备和线路时，不得进行其他工作，不得移开或越过遮拦，不论线路设备带电与否均应视为带电，不得靠近或触及设备和线路。

When inspecting high-voltage equipment and lines, inspection personnel shall not engage in other work, remove or cross barriers. All equipment and lines shall be treated as live regardless of whether they are actually energized, and personnel shall not approach or touch the equipment and lines.

6.3.8 雷雨天气， 需要巡视室外高压设备时， 应穿绝缘靴、 并不得靠近避雷器和避雷针。

During thunderstorms, if outdoor high-voltage equipment needs to be inspected, personnel shall wear insulated boots and keep away from lightning arresters and lightning rods.

6.3.9 高压设备发生接地时，室内不得接近故障点4m以内，室外不得接近故障点8m以内。进入上述范围人员应穿绝缘靴，接触设备的外壳和构架时，应戴绝缘手套。

When a grounding fault occurs in high-voltage equipment, people should not approach within 4 meters of the fault point indoors and within 8 meters of the fault point outdoors. Personnel entering the above-mentioned range should wear insulating boots, and when touching the outer casing and framework of the equipment, they should wear insulating gloves.

## 6.4 设备验收 Equipment acceptance

6.4.1 变配电站新建、扩建、技改、检修工作完成后，应验收合格方能投运。

After the completion of new construction, expansion, technical renovation, and maintenance work of substations and distribution stations, they can only be put into operation after passing the acceptance inspection.

6.4.2 新、改、扩变配电站的设计图纸、设备的原始资料、及验收记录应妥善收集并存档。

The design drawings of newly built, renovated, and expanded substations and distribution stations, the original materials of the equipment, and the acceptance records should be properly collected and filed.

## 6.5 设备缺陷管理Equipment defect management

6.5.1 变电站运行人员应对运行监控、巡视、检修及试验等工作中发现的设备缺陷进行分类管理:

Substation operating personnel shall implement classified management for equipment defects identified during operation monitoring, inspection, maintenance, and testing activities:

- 随时可能造成设备损坏、人身伤亡、大面积停电、火灾等事故的缺陷为危急缺陷，危急缺陷应立即采取措施处理。

Critical defects: defects that may immediately cause equipment damage, personal injury, large-scale power outages, fires, or other accidents. Critical defects must be addressed with immediate corrective measures.

- 对人身或设备有严重威胁、暂时尚能坚持运行但需尽快处理的缺陷为严重缺陷,严重缺陷应尽快(一个月内) 消除,并在处理前采取相应防范措施。

Major defects: defects that pose serious threats to personnel or equipment, which can temporarily remain in operation but require prompt resolution. Major defects shall be rectified as soon as possible (within one month), with appropriate preventive measures implemented prior to resolution.

- 情况较轻、对安全运行影响较小、可列入年度或季度检修计划中加以消除的缺陷为一般缺陷,一般缺陷应制定消除计划,并按计划处理。

Minor defects: defects with relatively minor impact on operational safety that can be incorporated into annual or quarterly maintenance plans. Minor defects shall be included in an elimination schedule and resolved according to the established plan.

6.5.2 缺陷处理验收后,运行人员应完成消缺记录,并定期开展设备缺陷分析工作。

Upon completion and verification of defect rectification, operating personnel shall document the defect resolution and conduct periodic equipment defect analysis.

## 6.6工作票、操作票Work permits and operation tickets

6.6.1 10/6kV 及以上电压等级的变配电站设备设施的检修、改装、调整、试验、校验等工作，应填写工作票。

For maintenance, modification, adjustment, testing, or calibration work on equipment and facilities in substations with voltage levels of 10/6kV or higher, a work permit must be filled out.

6.6.2 工作票由设备运行管理单位的电气负责人签发，或由经设备运行管理单位审核合格并批准的修试及基建单位的电气负责人签发。

The work permit shall be issued by the electrical supervisor of the equipment operation and management unit or by the electrical supervisor of the maintenance, testing, or construction unit that has been reviewed, qualified, and approved by the equipment operation and management unit.

6.6.3 工作票的种类和票面格式使用应符合 GB 26860 的要求。

The types and format of work permits shall comply with the requirements of GB 26860.

6.6.4 一张工作票中，工作票签发人、工作许可人和工作负责人三者不应为同一人。工作许可人中只有现场工作许可人（作为工作班成员之一，进行该工作任务所需现场操作及安全措施者）可与工作负责人兼任。若相互兼任，应具备相应的资质，并履行相应的安全责任。

On a single work permit, the issuer, the permitter, and the work supervisor shall not be the same person. Only the on-site permitter (who is a member of the work team and performs on-site operations and safety measures required for the task) may concurrently serve as the work supervisor. If roles are combined, the personnel must possess the appropriate qualifications and fulfill the corresponding safety responsibilities.

6.6.5 一个工作负责人不应同时执行两张及以上工作票。

A single work supervisor shall not execute two or more work permits simultaneously.

6.6.6 10/6kV及以上电压等级的变配电站运行中，需要改变运行方式或电气设备改变其工作状态时，应填写操作票。

During the operation of substations with voltage levels of 10/6kV or higher, if changes to the operational mode or the working state of electrical equipment are required, an operation ticket must be filled out.

6.6.7 操作票应使用统一的票面格式，并应符合《电力安全工作规程 发电厂和变电站电气部分》（GB 26860）的要求。

Operation tickets shall use a unified format and comply with the requirements of the Safety Code for Electric Power Work-Electrical Parts of Power Plants and Substations (GB 26860).

6.6.8操作票由操作人员填写，每张票填写一个操作任务。

Operation tickets shall be filled out by the operator, with one ticket for each operation task.

6.6.9 操作前应根据模拟图板（屏）或接线图核对所填写的操作项目，并经审核签名。

Before execution, the operation items on the ticket shall be verified against the mimic diagram (panel) or wiring diagram and reviewed and signed.

6.6.10 操作时应执行唱票和复诵，每操作完一步，应在操作项目前确认。操作执行结束，在最后一步下方加盖“已执行”章，章印不应掩压步骤项。作废操作票应在作废页“操作任务”栏内盖“作废”章，并在作废操作票首页“备注”栏内注明作废原因。

During operations, call-and-repeat procedures shall be executed. After completing each step, the operator shall confirm the item before proceeding. Upon completion of the operation, an "Executed" stamp shall be affixed below the final step, ensuring the stamp does not obscure the step details. For voided operation tickets, a "Void" stamp shall be placed in the "Operation Task" column of the voided page, and the reason for voiding shall be noted in the "Remarks" column on the first page.

6.6.11 下列项目应填入操作票：

The following items shall be recorded in the operation ticket:

- 拉、合断路器、隔离开关，检查断路器、隔离开关的位置；

Opening or closing circuit breakers and disconnectors, and verifying their positions.

- 拉、合接地刀闸，检查接地刀闸的位置；

Opening or closing grounding switches, and verifying their positions.

- 使用带电显示器进行验电，检查带电显示器显示是否正常；

Using a voltage detector to check for live circuits and verifying the detector's display.

- 验电、装拆接地线；

Checking for voltage presence and installing or removing grounding wires.

- 恢复送电前，检查待送电范围内短路接地线已拆除，接地刀闸已拉开；

Before restoring power, verifying that all short-circuit grounding wires within the power restoration range have been removed and grounding switches have been opened.

- 给上或取下控制回路、合闸回路或电压互感器二次回路熔断器，切换投退保护压板；

Insert or remove the fuses of the control circuit, closing circuit, or secondary circuit of the voltage transformer, and switch on or off the protection trip block.

- 检查设备或线路运行正常。

Checking that equipment or circuits are operating normally.

6.6.12 事故紧急处理、自动程序操作、拉合断路器或开关的单一操作，可不填写操作票。

No operation ticket is required for emergency fault handling, automated sequence operations, or single switching operations of circuit breakers/disconnectors.

## 6.7 倒闸操作Switching operations

6.7.1 倒闸操作应严格执行操作票制度，每张操作票只能填写一个操作任务。

Switching operations shall strictly comply with the operation ticket system. Only one operation task may be recorded per ticket.

6.7.2 倒闸操作必须根据值班调度员或值班负责人的指令，受令人复诵无误后执行。在发布和接受操作指令时，必须互报单位、姓名，严格执行发令、复诵、录音、汇报和记录制度，并使用统一的调度术语、操作术语和设备双重名称。

Switching operations must be executed based on the instructions of the shift dispatcher or the responsible operator on duty. The recipient shall repeat the instructions verbatim for confirmation before execution. During the issuance and receipt of operational commands, both parties must exchange their unit names and personal identities. Strict adherence to the command issuance, repetition, recording, reporting, and documentation system is mandatory. Unified dispatching terminology, operational terms, and dual device naming conventions shall be used.

6.7.3 倒闸操作必须两人进行，操作中发生疑问时应立即停止操作并汇报，弄清后再继续操作。

Switching operations must be performed by two personnel. If any doubt arises during the operation, it shall be immediately halted and reported. Operations may resume only after clarification.

6.7.4 为防止误操作，所有投运的闭锁装置不得随意退出或解锁。

To prevent mis-operations, all operational interlock devices in service shall not be arbitrarily bypassed or deactivated.

6.7.5 操作票填写应用钢笔或圆珠笔，字迹清楚正确，设备名称编号和状态、有关参数和时间、操作动词不得涂改。

Operation tickets shall be filled out using a pen or ballpoint pen, with legible and accurate handwriting. Device names, identification numbers, statuses, relevant parameters, timestamps, and operational verbs shall not be altered.

6.7.6 倒闸操作要有统一、确切的操作术语，正确使用合格的操作工具和安全工具。

Switching operations shall employ uniform and precise operational terminology, and only qualified operational tools and safety equipment shall be used.

6.7.7 使用操作票必须严格执行以下步骤：预受操作任务，明确操作目的；填写及审核操作票；正式发布和接受命令；模拟预演；现场核对设备名称，逐项唱票操作；复查、汇报并做好记录。

The following steps must be strictly followed when using operation tickets: Preliminary acceptance of the operation task and clarification of objectives. Completion and review of the operation ticket. Formal issuance and acceptance of commands. Simulation and rehearsal. On-site verification of device names, with step-by-step call-and-repeat execution. Post-operation review, reporting, and documentation.

6.7.8 严防发生下列误操作：误拉、合开关；带接地线合闸；带电装设接地线、带电合接地闸刀；带负荷拉、合闸刀；非同期并列。

The following mis-operations must be strictly prevented: Incorrect opening or closing of switches. Closing a circuit with grounding wires still connected. Installing grounding wires or closing grounding disconnectors on energized equipment. Opening or closing disconnectors under load. Non-synchronized paralleling.

6.7.9 不用开操作票的操作：

Operations exempt from requiring an operation ticket include:

- 事故处理

Emergency fault handling

- 拉合断路器（开关）的单一操作

Single switching operations (e.g., opening/closing a circuit breaker or switch)

- 拉开接地隔离开关（刀闸）或拆除全厂（所）仅有的一组接地线

Opening a grounding disconnector or removing the sole set of grounding wires in the entire facility

6.7.10 已执行的操作票保存六个月。

Executed operation tickets shall be retained for six months.

## 6.8 设备预防性试验Equipment preventive testing

6.8.1 变电站应按DL/T 596及参照DL/T 393标准开展设备预防性试验，按DL/T 995开展继电保护及安全自动装置检验，试验及检验工作应由具备相应资质的单位进行。

Substations shall conduct equipment preventive testing in accordance with DL/T 596 and reference DL/T 393 standards. Relay protection and safety automation device inspections shall be performed as per DL/T 995. Testing and inspection work shall be carried out by qualified entities with appropriate certifications.

6.8.2 参加电气试验人员，必须熟悉所用试验设备、 仪器的性能和使用方法，必须熟练掌握试验方法、程序和标准。

Personnel participating in electrical testing must be familiar with the performance and operation methods of all testing equipment and instruments. They must also thoroughly master testing procedures, methodologies, and standards.

6.8.3试验用的设备、仪器须经有关部门试验检定合格， 精度等级必须符合试验项目的要求。

Testing equipment and instruments must be inspected and certified by relevant authorities, with accuracy grades meeting the requirements of the test items.

6.8.4 固定的试验场所应设置各种必要的安全防护遮栏、安全警告牌、 灯光音响信号装置和安全联锁装置。在电气设备安装地点进行试验时，试验设备、被试品和试验连接线的周围设置临时遮拦，遮栏上应悬挂“止步！高压危险”警告牌。大型设备试验时还应有专人看守。

Fixed testing sites shall be equipped with necessary safety barriers, warning signs, audio-visual signal devices, and safety interlock systems. For on-site testing of electrical equipment, temporary barriers must be installed around the testing equipment, test objects, and connecting wires, with "Danger! High Voltage" warning signs prominently displayed. Large-scale equipment testing shall additionally require dedicated personnel for supervision.

6.8.5 变配电站应根据设备具体情况及上级对定期切换试验周期的要求，制订定期切换试验计划。

Substations shall develop periodic switching test plans based on equipment conditions and higher-level requirements for test cycles.

6.8.6 定期切换的试验设备和项目为：站用变、直流电源、事故照明、消防装置、事故音响信号、光字牌通讯系统等。

Regularly tested equipment and items include: station service transformers, DC power supplies, emergency lighting, fire protection systems, alarm signals, indicator panels, and communication systems.

6.8.7 对运行影响较大的试验切换工作，应安排在适当时候进行，试验切换前应做好事故预想，制订必要的安全对策，以防止出现异常情况时束手无策。

Tests with significant operational impact shall be scheduled appropriately. Pre-test contingency plans and necessary safety measures must be prepared to address potential abnormalities.

6.8.8 预防性试验之前，应由主管技术人员拟定试验方案， 划出试验接线圈，提出安全措施，交部门主管领导审核批准后由工作票签发人签发工作票，交试验班执行。

Prior to preventive testing, technical supervisors shall draft test plans, illustrate wiring diagrams, and propose safety measures. These must be reviewed and approved by department heads before work permits are issued by authorized personnel for execution by the testing team.

6.8.9 试验工作负责人应向全体试验人员详细说明试验任务、项目、标准、安全措施和注意事项，布置每个试验人员的任务和应负的责任，并记录备查。

The test supervisor shall brief all personnel on test objectives, items, standards, safety measures, and precautions, clearly assigning responsibilities. Detailed records shall be maintained for reference.

6.8.10 试验过程中的各项操作应严格按安全操作规程和试验程序进行。

All testing operations shall strictly comply with safety protocols and testing procedures.

6.8.11 每次试验切换后，应将试验切换情况在运行日志上详细记录。用户宜对设备试验数据与该设备标准值、出厂及历次试验数据比较,分析数据变化的规律和趋势，与同类设备数据比较,判断是否异常。

Post-test records shall be documented in operational logs. Equipment test data should be compared against standard values, factory data, and historical records to analyze trends. Cross-reference with similar equipment data helps identify abnormalities.

## 6.9 运行维护 Operation maintenance

6.9.1 运行人员应加强防误闭锁装置的运行、维护管理，确保防误闭锁装置齐全有效，并处于良好状态。

Operational staff shall enhance management of anti-mis-operation locking devices, ensuring their completeness, effectiveness, and proper functioning.

6.9.2 运行人员应加强变电站安防视频监控的运行管理。

Personnel shall strengthen operational management of substation security video surveillance systems.

6.9.3 运行人员应按季节性特点做好防风、防雷、防汛、防寒、防冰冻等工作，加强大风、暴雨、暴雪等恶劣天气下设备运行维护。

Seasonal preparedness for wind proofing, lightning protection, flood prevention, winterization, and anti-icing measures shall be implemented. Special attention shall be given to equipment maintenance during extreme weather (gales, rainstorms, blizzards).

6.9.4 变电室应开展设备污闪防治工作。

Substation rooms shall implement pollution flashover prevention measures.

6.9.5 应定期开展设备红外测温、油色谱分析和避雷器泄漏电流测试等试验工作。

Regular testing shall include infrared thermography, oil chromatography analysis, and lightning arrester leakage current measurements.

## 6.10 安保、环境管理Security and environmental management

6.10.1除变电所人员外进入变、配电所，必须填写登记表，并由内部人员带领方可入内；

Except for substation personnel, anyone entering the transformer or distribution station must fill out a registration form and be accompanied by internal staff.

6.10.2所有进入变电所的外来人员，必须遵守变电所规定，不得随意走动，进入设备间必须有运行人员陪同；

All external personnel entering the substation must comply with its regulations, refrain from moving around arbitrarily, and must be accompanied by operational staff when entering equipment rooms.

6.10.3其他无关人员一律不得擅自进入变电所，不准擅自让所外人员存放物品；

Unauthorized personnel are strictly prohibited from entering the substation, and no external items may be stored without permission.

6.10.4不准携带易燃易爆物品进入变电所；

Flammable or explosive materials are not allowed inside the substation.

6.10.5值班人员确认进入变电所的人精神状态良好，酒后禁止进入变电所；

Duty personnel must confirm that individuals entering the substation are in good mental condition, intoxicated persons are prohibited from entering.

6.10.6值班人员要提高警惕，发现可疑人员，应立即通知安保；

Duty personnel must remain vigilant and immediately notify security if suspicious individuals are detected.

6.10.7对不符合进入变电所条件的人员，值班员有权拒绝其进入；

Duty personnel have the authority to deny entry to anyone who does not meet the substation access requirements.

6.10.8进入人员必须服从值班人员指挥，在值班员进行倒闸操作时，跟该工作无关的人员必须退出变电所；

All entrants must follow the instructions of duty personnel. During switching operations, personnel unrelated to the task must exit the substation.

6.10.9 室内变压器、高压配电装置、低压配电装置的操作区、维护通道应铺设绝缘胶垫；

Insulated rubber mats must be laid in the operating and maintenance areas of indoor transformers, high-voltage distribution equipment, and low-voltage distribution equipment.

6.10.10 电缆沟盖板齐全，电缆夹层、电缆沟和电缆室设置的防水、排水措施完好有效；

Cable trench covers must be complete, and waterproofing and drainage measures in cable compartments, trenches, and rooms must be intact and functional.

6.10.11 设备构架、基础无严重腐蚀，房屋不漏雨，电缆、桥架穿墙的间隙用不燃材料封严密，无未封堵的孔洞、沟道；

Equipment frameworks and foundations must not exhibit severe corrosion, buildings must be leak-free, and gaps where cables or bridges pass through walls must be sealed with non-combustible materials, with no unsealed holes or ducts.

6.10.12 变配电站空气温度和湿度应符合GB/T 24274、DL/T 593的要求，设备区域内应配有温、湿度计；

The temperature and humidity in the substation must comply with GB/T 24274 and DL/T 593 standards, and the equipment area must be equipped with thermometers and hygrometers.

6.10.13有专人值班的变配电站应配备带有录音功能的专用电话，电话畅通，时钟准确；

Substations with dedicated duty personnel must be equipped with a dedicated telephone with recording functionality, ensuring clear communication and accurate timekeeping.

6.10.14 正常照明和应急照明系统应完好,疏散指示标志灯的持续照明时间应大于 30min；

Normal and emergency lighting systems must be fully functional, with evacuation indicator lights providing continuous illumination for at least 30 minutes.

6.10.15 对装有产生有毒气体、窒息性气体的配电装置的房间，在发生事故时房间内易聚集气体的部位，应装设强制向外排风装置；

Rooms housing distribution equipment that produces toxic or asphyxiating gases must be equipped with forced exhaust ventilation systems in areas prone to gas accumulation during accidents.

6.10.16 室内变配电装置布置、安全净距、通道与围栏等应符合 GB 50053、GB 50054、GB 50059、GB 50060等的要求；

The layout, safety clearances, passageways, and barriers of indoor distribution equipment must comply with GB 50053, GB 50054, GB 50059, GB 50060, and other relevant standards.

6.10.17部分停电的工作，工作人员与未停电设备安全距离不符合下表规定时应装设临时遮栏，表中未列电压等级按高一档电压等级安全距离，参考表1：

For partially de-energized work, temporary barriers must be installed if the safety distance between workers and live equipment does not meet the requirements listed in the table below. For voltage levels not listed, the safety distance of the next higher voltage level applies (Refer to Table 1).

表1 电压等级安全距离

Table 1 Voltage Level Safety Distances

| 电压等级 （KV） Voltage Level | 安全距离（M） Safety Distance |
| --- | --- |
| ≤10 | 0.70 |
| 35 | 1.00 |
| 110 | 1.5 |

6.10.18 变配电站门、窗及安全出口的设置应符合 GB 50053、GB 50352 等的要求，出入口应设置高度不低于400mm的防小动物挡板并采取其他防鼠措施；

Doors, windows, and emergency exits in substations must comply with GB 50053 and GB 50352 standards. Entrances must be fitted with anti-rodent barriers at least 400mm high, along with other rodent prevention measures.

6.10.19 变配电站内环境整洁，场地平整，设备间不应存放与运行无关的物品，不应有与其无关的管道和线路通过，巡视道路应畅通；

The substation environment must be clean and level. Equipment rooms must not store unrelated items or have unrelated pipelines or wiring passing through. Inspection pathways must remain unobstructed.

6.10.20 当变配电站设置在地下时，应采取防水措施。

For underground substations, waterproofing measures must be implemented.

## 6.11 安全工器具管理Safety tool management

6.11.1 变配电站应配备质量合格、数量满足工作需求的安全工器具，包括：绝缘安全工器具、登高作业安全工器具、检修工具、测量仪表。

Substations shall be equipped with qualified safety tools in sufficient quantities to meet operational needs, including: insulated safety tools, elevated work safety tools, maintenance tools, and measuring instruments.

6.11.2 安全工器具使用前应进行试验有效期的核查及外观检查，检查表面有无裂纹、划痕、毛刺、孔洞、断裂、有无老化迹象等；对安全工器具的机械、绝缘性能发生疑问时，应追加试验，合格后方可使用。

Before use, safety tools shall be checked for valid test dates and inspected for external defects such as cracks, scratches, burrs, holes, fractures, or signs of aging. If there are doubts about the mechanical or insulating performance of a safety tool, additional testing shall be conducted, and it shall only be used after passing inspection.

6.11.3 安全工器具应妥善保管，存放在干燥通风的场所，不允许当作其他工具使用，且不合格的安全工器具不应存放在工作现场。部分安全工器具还应符合下列要求：

Safety tools shall be properly stored in a dry and ventilated area, shall not be used for other purposes, and defective tools shall not be kept at the worksite. Some safety tools shall also meet the following requirements:

6.11.3.1 绝缘杆应悬挂或架在支架上，不应与墙或地面接触；

Insulating rods shall be hung or placed on brackets and shall not come into contact with walls or the ground.

6.11.3.2绝缘手套、绝缘靴应与其他工具仪表分开存放，避免直接碰触尖锐物体；

Insulating gloves and boots shall be stored separately from other tools and instruments to avoid direct contact with sharp objects.

6.11.3.3高压验电器应存放在防潮的匣内或专用袋内。

High-voltage voltage detectors shall be stored in moisture-proof cases or dedicated bags.

6.11.4 安全工器具应统一分类编号，定置存放并登记在专用记录簿内，做到账物相符，一一对应并及时地记录安全工器具的检查、试验情况，公用安全工器具应由专人负责管理。

Safety tools shall be uniformly categorized, numbered, and stored in designated locations, with records kept in a dedicated logbook to ensure consistency between records and physical inventory. Inspection and testing records shall be updated promptly. Shared safety tools shall be managed by designated personnel.

## 6.12 消防管理Fire safety management

6.12.1 应设置符合 GB 50140要求的适用电气火灾的消防设施、器材，并定期维护、检查和测试。现场消防设施、器材不应挪作他用，周围不应堆放杂物和其他设备；采用气体灭火系统的消防钢气瓶，应加装爆裂预警探测装置。

Firefighting facilities and equipment suitable for electrical fires, compliant with GB 50140, shall be installed and regularly maintained, inspected, and tested. On-site firefighting equipment shall not be repurposed, and no obstructions or other devices shall be placed around them. Gas fire suppression system cylinders shall be equipped with rupture early-warning detection devices.

6.12.2 灭火器的定期检查、维修、报废和更新应按 GB 50444的要求执行。

Regular inspection, maintenance, scrapping, and replacement of fire extinguishers shall comply with GB 50444.

6.12.3 变配电站应保持进出口及疏散通道畅通，不应堵塞或占用，室内严禁烟火，对动火作业应办理审批手续，严加管理。

Substation entrances, exits, and evacuation routes shall remain unobstructed and shall not be blocked or occupied. Open flames are strictly prohibited indoors, and hot work permits shall be obtained and strictly managed.

## 6.13 安全标志标示配置和使用管理Safety signage configuration and usage management

6.13.1 变配电站内各种标示应齐全、清楚、正确，设备上不应粘贴与运行无关的标示。

All signage in substations shall be complete, clear, and accurate. No irrelevant labels shall be attached to equipment.

6.13.2 安全标示牌的悬挂位置和式样应符合GB 2894的要求。

The placement and design of safety signs shall comply with GB 2894.

6.13.3 每面配电盘柜应标明路名和调度编号，双面维护的配电盘柜前和盘柜后均应标明路名和调度编号，且路名、编号应与模拟图板（屏）、自动化监控系统、运行资料等保持一致。

Each switchboard shall be labeled with its circuit name and dispatch number. For double-sided maintenance switchboards, both front and rear sides shall be labeled, and the names and numbers shall match those on mimic diagrams (panels), automated monitoring systems, and operational records.

6.13.4 配电装置前应标注警戒线，警戒线距配电装置应不小于800mm。

Warning lines shall be marked in front of power distribution equipment, maintaining a distance of at least 800mm from the equipment.

6.13.5 电缆的首端、末端和分支处应设标志牌。

Cable endpoints, terminals, and branch points shall be labeled with identification tags.

6.13.6 变配电站内的电气设备操作面板及维修盖板上应有“当心触电”警示标识。

Electrical equipment control panels and maintenance covers in substations shall display "Danger: Electric Shock" warning labels.

6.13.7 变配电站的出入口应设置明显的安全警示标志牌。

Clear safety warning signs shall be posted at substation entrances and exits.

6.13.8 安装有气体灭火系统的变配电室应在门口装设显示气体灭火工作状态的指示灯，并有相应的安全提示标识。

Substations equipped with gas fire suppression systems shall have status indicator lights installed at the entrance to display system operation status, along with corresponding safety warning signs.

7 附件Attachments

无None