特种设备管理制度

Special Equipment Management System

内部使用

在使用前，请和文档编写人员确认本文档为最新版本。

未经上海暻熠数据科技有限公司、上海暻耀网络技术有限公司书面许可，其它任何机构或个人不可传阅、引用或复制本文件的内容。

For Internal Use Only

Before using, check with the documentation writer to make sure this document is the latest version.

Without the written permission of Shanghai Waigaoqiao GDS Technology Development Co., Ltd., Shanghai Yungang GDS Technology Development Co., Ltd., or Shanghai Shuchang Technology Co., Ltd., no other organization or individual is allowed to circulate, quote or copy the content of this document.

| 文件编号Documents | IP-PJ-EHS-10 |
| --- | --- |
| 版 本Edition | V1.0 |
| 文件维护部门File maintenance department | 上海浦江数据中心 |
| 会签部门Document Signing department | 上海浦江数据中心 |
| 执行范围Scope of execution | 上海浦江数据中心 |

文件修订记录

Document revision record

| 版本号 Edition | 版本日期 Date | 修订内容 Revised Content | 修订人员 Revision personnel | 核准员 Approver | 备注 Remarks |
| --- | --- | --- | --- | --- | --- |
| V1.0 | 2025-04-16 | 首次修订 | 楚靖岳 | 陆磊 |  |

目录Content

1 目的Purpose	4

2 适用范围Scope of application	4

3 规范性引用文件Reference documents	4

4 术语和定义Terms and definitions	5

5 职责Responsibility	6

5.1 特种设备安全总监Special Equipment Safety Director	6

5.2 特种设备安全员Special Equipment Safety Officer	8

6 程序Procedures	10

6.1 特种设备的使用Use of Special Equipment	10

6.2 特种设备的检验Inspection of Special Equipment	11

6.3 压力容器的安全附件校验周期Verification cycle of safety accessories for pressure vessels	11

6.5 教育培训Safety inspection of special equipment	14

6.6 事故报告Accident Report	14

6.7 特种设备的变更Changes to Special Equipment	14

7 附件Attachments	15

1 目的Purpose

本制度旨在建立上海暻熠数据科技有限公司、上海暻耀网络技术有限公司（以下简称“上海浦江数据中心”）特种设备管理流程。目标包括确保遵守国家和地方法律法规、国外相关法规、客户要求以及上海浦江数据中心内部要求，确保特种设备管理合规，降低运营EHS风险，并促进持续改进。

This system aims to establish the special equipment management process for Shanghai Waigaoqiao GDS Technology Development Co., Ltd., Shanghai Yungang GDS Technology Development Co., Ltd., and Shanghai Shuchang Technology Co., Ltd. (Below referred to as "SHANGHAI PUJIANG Data Center"). The objectives include ensuring compliance with national and local laws and regulations, relevant foreign regulations, customer requirements, and internal requirements of SHANGHAI PUJIANG Data Center, ensuring compliance with special equipment management, reducing operational EHS risks, and promoting continuous improvement.

2 适用范围Scope of application

适用于上海浦江数据中心，以及所有与EHS有关事项的管理职能。

Applicable to SHANGHAI PUJIANG Data Center and all management functions related to EHS matters.

3 规范性引用文件Reference documents

《中华人民共和国特种设备安全法》（2014年1月1日起施行）

Special Equipment Safety Law of the People's Republic of China (implemented on January 1, 2014)

《特种设备安全监察条例》（2009年修订）

Regulations on Safety Supervision of Special Equipment (Revised in 2009)

《特种设备事故报告和调查处理规定》（2022年3月1日起施行）

Regulations on Reporting and Investigating Special Equipment Accidents (to be implemented from March 1, 2022)

《特种设备使用单位落实使用安全主体责任监督管理规定》（国家市场监督管理总局令第

74号）

Regulations on the Supervision and Management of the Implementation of Safety Main Responsibility by Special Equipment Users (Order No. 74 of the State Administration for Market Regulation)

TSG 08  特种设备使用管理规则

TSG 08 Special Equipment Usage Management Rules

TSG 23  气瓶安全技术规程

TSG 23 Gas Cylinder Safety Technical Regulations

TSG 21  固定式压力容器安全技术监察规程

TSG 21 Safety Technical Supervision Regulations for Fixed Pressure Vessels

JJG 52  弹性元件式一般压力表、压力真空表和真空表检定规程

JJG 52 Verification Regulations for General Pressure Gauge, Pressure Vacuum Gauge and Vacuum Gauge with Elastic Element Type

《特种设备目录》（质检总局关于修订《特种设备目录》的公告2014年第114号）

Special Equipment Catalogue (Announcement No. 114 of 2014 by the General Administration of Quality Supervision, Inspection and Quarantine on the Revision of the Special Equipment Catalogue)

4 术语和定义Terms and definitions

4.1特种设备Special equipment

指对人身和财产安全有较大危险性的锅炉、压力容器（含气瓶）、压力管道、电梯、起重机械、客运索道、大型游乐设施、场（厂）内专用机动车辆。

Refers to boilers, pressure vessels (including gas cylinders), pressure pipeline, elevators, lifting crane, passenger ropeways, large amusement facilities, and industrial vehicles that pose significant risks to personal and property safety.

4.2压力容器Pressure vessel

是指盛装气体或者液体，承载一定压力的密闭设备，其范围规为最高工作压力大于或者等于 0.1MPa（表压）的气体、液化气体和最高工作温度高于或者等于标 准沸点的液体、容积大于或者等于 30L 且内直径(非圆形截面指截面内边界最大几何尺寸) 大于或者等于 150mm 的固定式容器和移动式容器；盛装公称工作压力大于或者等于 0.2MPa（表压），且压力与容积的乘积大于或者等于 1.0MPa•L 的气体、液化气体和标准 沸点等于或者低于 60℃液体的气瓶；氧舱。

It refers to enclosed equipment that contains gases or liquids and carries a certain pressure. Its scope is defined as gases with a maximum working pressure greater than or equal to 0.1 MPa (gauge pressure), liquefied gases, liquids with a maximum working temperature greater than or equal to the standard boiling point, fixed and mobile containers with a volume greater than or equal to 30 L and an inner diameter (non-circular cross-section refers to the maximum geometric dimension of the inner boundary of the cross-section) greater than or equal to 150 mm; Gas cylinders containing gases with a nominal working pressure greater than or equal to 0.2 MPa (gauge pressure) and a product of pressure and volume greater than or equal to 1.0 MPa • L, liquefied gases, and liquids with a standard boiling point equal to or lower than 60 ℃; Oxygen chamber.

4.3电梯Elevator

指动力驱动，利用沿刚性导轨运行的箱体或者沿固定线路运行的梯级（踏步）， 行升降或者平行运送人、货物的机电设备，包括载人（货）电梯、自动扶梯、自动人行 道等。非公共场所安装且仅供单一家庭使用的电梯除外。

Refers to power driven mechanical and electrical equipment that uses a box running along a rigid guide rail or steps running along a fixed line to lift or transport people and goods in parallel, including passenger (cargo) elevators, escalators, moving walkways, etc. Except for elevators installed in non-public places and only for single household use.

4.4气瓶Gas cylinder

用于环境温度为-40℃~60℃(注 1-1)、公称容积为 0.4L~3000L公称工作压力为 0.2MPa~70MPa(表压，下同),并且压力与容积的乘积大于或者等于 1.0MPa·L，盛装压缩气体、高(低)压液化气体、低温液化气体、溶解气体、吸附气体、混合气体(注 1-2)以及标准沸点等于或者低于 60℃的液体的无缝气瓶、焊接气瓶、低温绝热气瓶、纤维缠绕气瓶、内部装有填料的气瓶。

Seamless gas cylinders, welded gas cylinders, low-temperature insulated gas cylinders, fiber wound gas cylinders, and gas cylinders filled with fillers are used for environments with temperatures ranging from -40 ℃ to 60 ℃ (Note 1-1), nominal volumes ranging from 0.4L to 3000L, nominal working pressures ranging from 0.2MPa to 70MPa (gauge pressure, the same below), and a product of pressure and volume greater than or equal to 1.0MPa · L.

5 职责Responsibility

5.1 特种设备安全总监Special Equipment Safety Director

5.1.1压力容器职责Responsibilities of pressure vessels：

- 组织宣传、贯彻压力容器有关的法律法规、安全技术规范及相关标准；

Organize publicity and implementation of laws, regulations, safety technical specifications, and relevant standards related to pressure vessels.

- 组织制定上海浦江数据中心压力容器使用安全管理制度，督促落实压力容器使用安全责任制，组织开展压力容器安全合规管理；

Organize the development of a safety management system for the use of pressure vessels in SHANGHAI PUJIANG Data Center, supervise the implementation of the safety responsibility system for the use of pressure vessels, and organize the implementation of pressure vessel safety compliance management.

- 组织制定压力容器事故应急专项预案并开展应急演练；

Organize the development of emergency response plans for pressure vessel accidents and conduct emergency drills.

- 落实压力容器安全事故报告义务，采取措施防止事故扩大；

Implement the obligation to report pressure vessel safety accidents and take measures to prevent accidents from escalating.

- 对压力容器安全员进行安全教育和技术培训，监督、指导压力容器安全员做好相关工作；

Provide safety education and technical training to pressure vessel safety officers, supervise and guide them to do relevant work well.

- 按照规定组织开展压力容器使用安全风险评价工作，拟定并督促落实压力容器使用安全风险防控措施；

Organize and carry out safety risk assessment for the use of pressure vessels in accordance with regulations, formulate and supervise the implementation of safety risk prevention and control measures for the use of pressure vessels.

- 对上海浦江数据中心压力容器使用安全管理工作进行检查，及时向主要负责人报告有关情况，提出改进措施；

Inspect the safety management of pressure vessels in SHANGHAI PUJIANG Data Center, report relevant situations to the main responsible person in a timely manner, and propose improvement measures.

- 接受和配合有关部门开展压力容器安全监督检查、监督检验、定期检验和事故调查等工作，如实提供有关材料；

Accept and cooperate with relevant departments to carry out safety supervision and inspection, supervision and inspection, regular inspection, and accident investigation of pressure vessels, and truthfully provide relevant materials.

- 履行市场监督管理部门规定和本单位要求的其他压力容器安全管理职责。

Fulfill other safety management responsibilities for pressure vessels as stipulated by the market supervision and management department and required by our unit.

5.1.2电梯职责Elevator Responsibilities:

- 组织宣传、贯彻电梯有关的法律法规、安全技术规范及相关标准；

Organize publicity and implementation of elevator related laws, regulations, safety technical specifications, and relevant standards.

- 组织制定上海浦江数据中心电梯使用安全管理制度，督促落实电梯使用安全责任制，组织开展电梯安全合规管理；

Organize the development of a safety management system for the use of elevators in SHANGHAI PUJIANG Data Center, supervise the implementation of the elevator safety responsibility system, and organize the implementation of elevator safety compliance management.

- 组织制定电梯事故应急专项预案并开展应急演练；

Organize the development of emergency special plans for elevator accidents and conduct emergency drills.

- 落实电梯安全事故报告义务，采取措施防止事故扩大；

Implement the obligation to report elevator safety accidents and take measures to prevent accidents from escalating.

- 对电梯安全员进行安全教育和技术培训，监督、指导电梯安全员做好相关工作；

Provide safety education and technical training to elevator safety officers, supervise and guide them to do relevant work well.

- 按照规定组织开展电梯使用安全风险评价工作，拟定并督促落实电梯使用安全风险防控措施；

Organize and carry out elevator safety risk assessment in accordance with regulations, formulate and supervise the implementation of elevator safety risk prevention and control measures.

- 对上海浦江数据中心电梯使用安全管理工作进行检查，及时向主要负责人报告有关情况，提出改进措施；

Inspect the safety management of elevators in SHANGHAI PUJIANG Data Center, report relevant situations to the main responsible person in a timely manner, and propose improvement measures.

- 接受和配合有关部门开展电梯安全监督检查、监督检验、定期检验和事故调查等工作，如实提供有关材料；

Accept and cooperate with relevant departments to carry out elevator safety supervision and inspection, supervision and inspection, regular inspection, and accident investigation, and truthfully provide relevant materials.

- 上海浦江数据中心投保电梯保险的，落实相应的保险管理职责；

If SHANGHAI PUJIANG Data Center purchases elevator insurance, corresponding insurance management responsibilities shall be implemented.

- 履行市场监督管理部门规定和上海浦江数据中心要求的其他电梯使用安全管理职责。

Fulfill other elevator safety management responsibilities as required by market supervision and management departments and SHANGHAI PUJIANG Data Center.

5.1.3资格要求Qualification Requirements

5.1.3.1特种设备安全总监应当取得相应的特种设备安全管理人员资格证书。

The director of special equipment safety shall obtain the corresponding qualification certificate for special equipment safety management personnel.

5.2 特种设备安全员Special Equipment Safety Officer

5.2.1压力容器职责Responsibilities of pressure vessels：

- 建立健全压力容器安全技术档案并办理本单位压力容器使用登记；

Establish and improve safety technical files for pressure.

- 组织制定压力容器安全操作规程；

Organize the development of safety operating procedures for pressure vessels.

- 组织对压力容器作业人员和技术人员进行教育和培训；

Organize education and training for pressure vessel operators and technicians.

- 组织对压力容器进行日常巡检，纠正和制止违章作业行为；

Organize daily inspections of pressure vessels, correct and stop illegal operations.

- 编制压力容器定期检验计划，督促落实压力容器定期检验和后续整改等工作；

Develop a regular inspection plan for pressure vessels, supervise the implementation of regular inspections and subsequent rectification work for pressure vessels.

- 按照规定报告压力容器事故，参加压力容器事故救援，协助进行事故调查和善后处理；

Report pressure vessel accidents according to regulations, participate in pressure vessel accident rescue, assist in accident investigation and aftermath handling.

- 履行市场监督管理部门规定和本单位要求的其他压力容器使用安全管理职责。

Fulfill other safety management responsibilities for the use of pressure vessels as stipulated by the market supervision and management department and required by our unit.

5.2.2电梯职责Elevator Responsibilities

建立健全电梯安全技术档案并办理本单位电梯使用登记：

Establish and improve elevator safety technical files and handle the registration of elevator use in our unit:

- 组织制定电梯安全操作规程；

Organize the development of elevator safety operating procedures.

- 妥善保管电梯专用钥匙和工具；

Properly keep elevator specific keys and tools.

- 组织对电梯作业人员和技术人员进行教育和培训；

Organize education and training for elevator operators and technicians.

- 对电梯进行日常巡检，引导和监督正确使用电梯；

Conduct daily inspections of elevators, guide and supervise the correct use of elevators.

- 对电梯维护保养过程和结果进行监督确认，配合做好现场安全工作；

Supervise and confirm the maintenance process and results of elevators, and cooperate with on-site safety work.

- 确保电梯紧急报警装置正常使用，保持电梯应急救援通道畅通，在发生故障和困人等突发情况时，立即安抚相关人员，并组织救援；

Ensure the normal use of the elevator emergency alarm device, keep the elevator emergency rescue passage unobstructed, and immediately comfort relevant personnel and organize rescue in case of emergencies such as malfunctions and trapped people.

- 编制电梯自行检测和定期检验计划，督促落实电梯自行检测、定期检验和后续整改等工作；

Develop elevator self-inspection and regular inspection plans, supervise the implementation of elevator self-inspection, regular inspection, and subsequent rectification work.

- 按照规定报告电梯事故，参加电梯事故救援，协助进行事故调查和善后处理；

Report elevator accidents according to regulations, participate in elevator accident rescue, assist in accident investigation and aftermath handling.

- 履行市场监督管理部门规定和本单位要求的其他电梯使用安全管理职责。

Fulfill other elevator safety management responsibilities as stipulated by the market supervision and management department and required by our unit.

5.2.3资格要求Qualification Requirements

5.2.3.1上海浦江数据中心使用特种设备符合下列条件之一时，应配备专职安全管理人员，并且取得相应的特种设备安全管理人员资格证书：

When using special equipment in SHANGHAI PUJIANG Data Center that meets one of the following conditions, dedicated security management personnel should be equipped, and obtain the corresponding qualification certificate for special equipment safety management personnel:

- 使用额定工作压力大于或者等于 2.5MPa锅炉的；

Using boilers with a rated working pressure greater than or equal to 2.5 MPa.

- 使用5台以上(含5台)第Ⅲ类固定式压力容器的；

Using 5 or more (including 5) Class III fixed pressure vessels.

- 从事移动式压力容器或者气瓶充装的；

Engaged in the filling of mobile pressure vessels or gas cylinders.

- 使用 10 公里以上(含 10 公里)工业管道的；

Using industrial pipelines over 10 kilometers (including 10 kilometers).

- 使用移动式压力容器，或者客运拖牵索道，或者大型游乐设施的；

Using mobile pressure vessels, passenger towing cable cars, or large amusement facilities.

- 使用各类特种设备(不含气瓶)总量 20 台以上(含 20 台)的。

Using a total of 20 or more special equipment (excluding gas cylinders).

- 除前款规定以外的上海浦江数据中心可以配备兼职安全管理员，也可以委托具有特种设备安全管理人员资格的人员负责使用管理。

Except as provided in the preceding paragraph, SHANGHAI PUJIANG Data Center may be equipped with part-time security administrators or may entrust personnel with special equipment security management qualifications to be responsible for usage and management.

# 6 程序Procedures

## 6.1 特种设备的使用Use of Special Equipment

6.1.1上海浦江数据中心应当在特种设备投入使用前或者投入使用后三十日内，向负责特种设备安

全监督管理的部门办理使用登记，取得使用登记证书。

SHANGHAI PUJIANG Data Center shall, before or within thirty days after the special equipment is put into use, report to the responsible personnel for the safety of the special equipment

The department responsible for full supervision and management shall handle the use registration and obtain the use registration certificate.

6.1.2登记标志应当置于该特种设备的显著位置。

The registration mark should be placed in a prominent position on the special equipment.

6.1.3电梯的日常维护保养必须由依照本条例取得许可的安装、改 造、维修单位或者电梯制造单位进行。电梯应当至少每15日进行一次清洁、润滑、调整和检查。

The daily maintenance of elevators must be carried out by installation, renovation, maintenance units or elevator manufacturing units that have obtained permits in accordance with this regulation. Elevators should be cleaned, lubricated, adjusted, and inspected at least once every 15 days.

6.1.4上海浦江数据中心的压力容器和电梯的安装、改造、重大修理过程，应当经特种设备检验机构按照安全技术规范的要求进行监督检验；未经监督检验或者监督检验不合格的，不得使用。

The installation, renovation, and major repairs of pressure vessels and elevators in SHANGHAI PUJIANG Data Center shall be supervised and inspected by special equipment inspection agencies in accordance with safety technical specifications; Those that have not undergone supervision and inspection or have failed supervision and inspection shall not be used.

6.1.5上海浦江数据中心应当建立特种设备安全技术档案，安全技术档案应当包括以下内容:

SHANGHAI PUJIANG Data Center shall establish special equipment safety technology files, which shall include the following contents:

- 特种设备的设计文件、产品质量合格证明、安装及使用维护保养说明、监督检验证明等相关技术资料和文件；

Design documents, product quality certificates, installation and maintenance instructions, supervision and inspection certificates and other relevant technical information and documents for special equipment.

- 特种设备的定期检验和定期自行检查记录；

Regular inspection and self-inspection records of special equipment.

- 特种设备的日常使用状况记录；

Daily usage records of special equipment.

- 特种设备及其附属仪器仪表的维护保养记录；

Maintenance records of special equipment and its associated instruments and meters.

- 特种设备的运行故障和事故记录。

Record of operational failures and accidents of special equipment.

6.1.6气瓶安全管理按照《气瓶安全技术规程》(TSG 23)第8.5条执行,定期检验按照《气瓶安全技术规程》第9条执行。

Gas cylinder safety management shall be carried out in accordance with Article 8.5 of the Gas Cylinder Safety Technical Regulations (TSG 23), and regular inspections shall be carried out in accordance with Article 9 of the Gas Cylinder Safety Technical Regulations.

6.2 特种设备的检验Inspection of Special Equipment

6.2.1上海浦江数据中心应当按照安全技术规范的要求，在压力容器和电梯检验合格有效期届满前一个月向特种设备检验机构提出定期检验要求。未经定期检验或者检验不合格的特种设备，不得继续使用。

SHANGHAI PUJIANG Data Center shall, in accordance with the requirements of security technical specifications, submit regular inspection requirements to the special equipment inspection agency one month before the expiration of the validity period of pressure vessel and elevator inspection. Special equipment that has not undergone regular inspections or has failed inspections shall not continue to be used.

6.3 压力容器的安全附件校验周期Verification cycle of safety accessories for pressure vessels

6.3.1安全阀：1年/次校验。

Safety valve: calibrated once a year.

6.3.2压力容器上的压力表：半年/次。

Pressure gauges on pressure vessels: every six months。

6.4 特种设备的安全检查Safety inspection of special equipment

6.4.1上海浦江数据中心应当建立《压力容器安全风险管控清单》（见附件1）。

SHANGHAI PUJIANG Data Center shall establish a "Pressure Vessel Safety Risk Control Checklist" (see Attachment 1).

6.4.2特种设备安全员根据《压力容器安全风险管控清单》按照相关安全技术规范和上海浦江数据中心安全管理制度的要求，对投入使用的压力容器进行巡检，形成《每日压力容器安全检查记录》（见附件2）。

The special equipment safety officer shall inspect the pressure vessels put into use in accordance with the relevant safety technical specifications and the requirements of the SHANGHAI PUJIANG Data Center safety management system based on the "Pressure Vessel Safety Risk Control List" and form the "Daily Pressure Vessel Safety Inspection Record" (see Attachment 2).

6.4.3 特种设备安全总监要每周至少组织一次风险隐患排查，分析研判压力容器使用安全管理情况，研究解决每日管控中发现的问题，形成《每周压力容器安全排查治理报告》。（见附件3）

The Special Equipment Safety Director shall organize at least one risk and hazard investigation per week, analyze and judge the safety management of pressure vessel use, study and solve the problems found in daily control, and form the "Weekly Pressure Vessel Safety Investigation and Governance Report". (See Attachment 3)

6.4.4上海浦江数据中心应当建立压力容器安全月调度制度。主要负责人要每月至少听取一次特种设备安全总监工作情况汇报，对当月压力容器安全日常管理、风险隐患排查治理等情况进行总结，对下个月重点工作做出调度安排，形成《每月压力容器安全调度会议纪要》（见附件4）。

SHANGHAI PUJIANG Data Center shall establish a monthly scheduling system for pressure vessel safety. The main person in charge shall listen to the work report of the special equipment safety director at least once a month, summarize the daily management of pressure vessel safety and the investigation and treatment of risk hazards in the current month, make scheduling arrangements for the key work of the next month, and form the "Monthly Pressure Vessel Safety Scheduling Meeting Minutes" (see Attachment 4).

6.4.5上海浦江数据中心应当将主要负责人、特种设备安全总监和特种设备安全员的设立、调整情况，《压力容器安全风险管控清单》《压力容器安全总监职责》《压力容器安全员守则》以及压力容器安全总监、压力容器安全员提出的意见建议、报告和问题整改落实等履职情况予以记录并存档备查。

SHANGHAI PUJIANG Data Center shall record and archive the establishment and adjustment of the main responsible person, special equipment safety director, and special equipment safety officer, as well as the performance of the "Pressure Vessel Safety Risk Control List", "Responsibilities of Pressure Vessel Safety Director", "Code of Conduct for Pressure Vessel Safety Officer", and the opinions, suggestions, reports, and problem rectification implementation proposed by the Pressure Vessel Safety Director and Pressure Vessel Safety Officer.

6.4.6上海浦江数据中心应当制定《电梯安全风险管控清单》（见附件5）。

SHANGHAI PUJIANG Data Center shall develop an "Elevator Safety Risk Control Checklist" (see Attachment 5).

6.4.7特种设备安全员要每日根据《电梯安全风险管控清单》，按照相关安全技术规范和本单位安全管理制度的要求，对投入使用的电梯进行巡检，形成《每日电梯安全检查记录》（见附件6），对发现的安全风险隐患，应当立即通知电梯维护保养单位予以整改，及时上报特种设备安全总监或者单位主要负责人。未发现问题的，也应当予以记录，实行零风险报告。

The special equipment safety officer shall conduct daily inspections of the elevators put into use in accordance with the "Elevator Safety Risk Control List", relevant safety technical specifications, and the requirements of the unit's safety management system, and form a "Daily Elevator Safety Inspection Record" (see Attachment 6). If any safety risks or hidden dangers are found, the elevator maintenance unit shall be immediately notified to rectify them, and the special equipment safety director or the main person in charge of the unit shall be promptly reported. If no problems are found, they should also be recorded and a zero risk report should be implemented.

6.4.8特种设备安全总监要每周至少组织一次风险隐患排查，分析研判电梯使用安全管理情况，研究解决日管控中发现的问题，形成《每周电梯安全排查治理报告》。特种设备安全总监应当对维护保养过程进行全过程或者抽样监督，并做出记录，发现问题的应当及时处理（见附件7）。

The safety director of special equipment shall organize at least one risk and hazard investigation per week, analyze and judge the safety management of elevator use, study and solve the problems found in daily control, and form the "Weekly Elevator Safety Investigation and Governance Report". The safety director of special equipment shall conduct full process or sampling supervision of the maintenance process and make records. Any problems found shall be dealt with in a timely manner (see Attachment 7).

6.4.9上海浦江数据中心应当建立电梯安全月调度制度。主要负责人要每月至少听取一次电梯安全总监管理工作情况汇报，对当月电梯安全日常管理、风险隐患排查治理等情况进行总结， 对下个月重点工作做出调度安排，形成《每月电梯安全调度会议纪要》（见附件8）。

SHANGHAI PUJIANG Data Center shall establish a monthly elevator safety dispatch system. The main person in charge shall listen to a report on the management work of the elevator safety director at least once a month, summarize the daily management of elevator safety and the investigation and treatment of risks and hidden dangers in the current month, make scheduling arrangements for the key work of the next month, and form the "Monthly Elevator Safety Scheduling Meeting Minutes" (see Attachment 8).

6.4.10上海浦江数据中心应当将主要负责人、特种设备安全总监和特种设备安全员的设立、调整情况，《电梯安全风险管控清单》《电梯安全总监职责》《电梯安全员守则》以及特种设备安全总监、特种设备安全员提出的意见建议、报告和问题整改落实等履职情况予以记录并存档备查。

SHANGHAI PUJIANG Data Center shall record and archive the establishment and adjustment of the main responsible person, special equipment safety director, and special equipment safety officer, as well as the performance of the "Elevator Safety Risk Control List ", "Responsibilities of Elevator Safety Director", "Code of Conduct for Elevator Safety Officers", and the opinions, suggestions, reports, and implementation of problem rectification proposed by the special equipment safety director and special equipment safety officer.

## 6.5 教育培训Safety inspection of special equipment

6.5.1上海浦江数据中心应当对特种设备安全总监和特种设备安全员进行法律法规、标准和专业知识培训、考核，同时对培训、考核情况予以记录并存档备查。

SHANGHAI PUJIANG Data Center shall provide legal, regulatory, standard, and professional knowledge training and assessment to the Special Equipment Safety Director and Special Equipment Safety Officer, and record and archive the training and assessment results for future reference.

## 6.6 事故报告Accident Report

6.6.1特种设备发生事故后，事故现场有关人员应当立即向特种设备安全总监报告；特种设备安全总监接到报告后，应当于 1小时内向事故发生地的县级以上市场监督管理部门和有关部门报告。情况紧急时，事故现场有关人员可以直接向事故发生地的县级以上市场监督管理部门报告。

After a special equipment accident occurs, relevant personnel at the accident site shall immediately report to the Special Equipment Safety Director; After receiving the report, the special equipment safety director shall report to the county-level or above market supervision and management department and relevant departments in the place where the accident occurred within one hour. In case of emergency, relevant personnel at the scene of the accident can directly report to the county-level or above market supervision and management department where the accident occurred.

6.6.2事故报告应当包括以下内容The accident report shall include the following contents:

- 事故发生的时间、地点、单位概况以及特种设备种类；

The time, location, unit profile, and type of special equipment of the accident.

- 事故发生简要经过、现场破坏情况、已经造成或者可能造成的伤亡和涉险人数、初步估计的直接经济损失；

Brief description of the accident, on-site damage, casualties and number of people at risk that have been or may be caused, and preliminary estimated direct economic losses.

- 已经采取的措施；

Measures already taken.

- 报告人姓名、联系电话；

Name and contact phone number of the reporter.

- 其他有必要报告的情况。

Other situations that require reporting.

## 6.7 特种设备的变更Changes to Special Equipment

6.7.1特种设备的变更登记包括：改造变更、移装变更、单位变更、更名变更、达到设计使用年限继续使用的变更、不得申请办理移装变更、单位变更的情况、停用、报废等变更手续需按照《特种设备使用管理规则》3.8条内容执行。

The registration of changes in special equipment includes renovation changes, relocation changes, unit changes, renaming changes, changes that continue to be used after reaching the design service life, situations where relocation changes cannot be applied for, unit changes, suspension, scrapping and other change procedures, which shall be carried out in accordance with Article 3.8 of the "Special Equipment Use Management Rules"

7 附件Attachments

- IF-PJ-EHS-1001:《压力容器安全风险管控清单》Pressure Vessel Safety Risk Control List

- IF-PJ-EHS-1002:《每日压力容器安全检查记录》Daily Pressure Vessel Safety Inspection Record

- IF-PJ-EHS-1003:《每周压力容器安全排查治理报告》Weekly Pressure Vessel Safety Inspection and Management Report

- IF-PJ-EHS-1004:《每月压力容器安全调度会议纪要》Monthly Pressure Vessel Safety Dispatch Meeting Minutes

- IF-PJ-EHS-1005:《电梯安全风险管控清单》Elevator Safety Risk Control List

- IF-PJ-EHS-1006:《每日电梯安全检查记录》Daily Elevator Safety Inspection Record

- IF-PJ-EHS-1007:《每周电梯安全排查治理报告》Weekly Elevator Safety Inspection and Management Report

- IF-PJ-EHS-1008:《每月电梯安全调度会议纪要》Monthly Elevator Safety Dispatch Meeting Minutes

- IF-PJ-EHS-1009:《特种设备管理台账》Special Equipment Management Log