高风险作业管理制度

High-risk Operation Management System

内部使用

在使用前，请和文档编写人员确认本文档为最新版本。

未经上海暻熠数据科技有限公司、上海暻耀网络技术有限公司书面许可，其它任何机构或个人不可传阅、引用或复制本文件的内容。

Internal use

Before using, check with the documentation writer to make sure this document is the latest version.

Without the written permission of SHANGHAI Data Technology Co., LTD., no other organization or individual is allowed to circulate, quote or copy the content of this document.

| 文件编号 Documents | IP-PJ-EHS-11 |
| --- | --- |
| 版 本 Edition | V1.0 |
| 文件维护部门File maintenance department | 上海浦江数据中心 |
| 会签部门 Document Signing department | 上海浦江数据中心 |
| 执行范围 Scope of execution | 上海浦江数据中心 |

文件修订记录

Document revision record

| 版本号 Edition | 版本日期 Date | 修订内容 Revised Content | 修订人员 Revision personnel | 核准员 Approver | 备注 Remarks |
| --- | --- | --- | --- | --- | --- |
| V1.0 | 2025-04-16 | 首次修订 | 楚靖岳 | 陆磊 |  |

目录Content

1	目的 Purpose	4

2	适用范围 Scope of application	4

3	规范性引用文件 Reference documents	4

4	术语与定义 Terms and definitions	5

5	职责 Responsibilities	6

5.1 EHS管理负责人 EHS management officer	6

6	程序 Procedures	6

6.1 高风险作业范围 Scope of high risk operations	6

6.2 高风险作业审批 Approval of high risk operation	6

6.3 管理要求 Management requirements	7

6.4 作业变更 Change management	28

7附件 Attachments	28

- 目的 Purpose

为加强上海暻熠数据科技有限公司、上海暻耀网络技术有限公司（以下简称“上海浦江数据中心”）高风险作业的安全管理。目标包括遵守国家和地方法律法规、国外相关法规、客户要求以及上海浦江数据中心内部要求，控制和消除高风险作业的潜在风险，减少和避免高风险作业中各类事故的发生，实现安全生产、运营，特制定本制度。

To strengthen the security management of high-risk operations of SHANGHAI Data Technology Co., LTD. (hereinafter referred to as "SHANGHAI Data Center"). The objectives include complying with national and local laws and regulations, relevant foreign regulations, customer requirements and internal requirements of SHANGHAI PUJIANG Data Center, controlling and eliminating the potential risks of high-risk operations, reducing and avoiding the occurrence of various accidents in high-risk operations, realizing safe production and operation, and formulating this system.

- 适用范围 Scope of application

本制度适用于上海浦江数据中心各部门以及相关方在所从事的满足以下高风险作业定义的作业活动。

This system applies to all departments of SHANGHAI PUJIANG Data Center and relevant parties engaged in the operation activities that meet the following high-risk operation definition.

- 规范性引用文件 Reference documents

《中华人民共和国安全生产法》（2021年修订）

Work Safety Law of the People's Republic of China (revised in 2021)

《工贸企业有限空间作业安全规定》（中华人民共和国应急管理部令（第13号））

Regulations on Safety in Confined Space Operation of Industrial and Trade Enterprises (Decree of the Ministry of Emergency Management of the People's Republic of China No. 13)

GB 6067     起重机械安全规程

GB6067 	   Safety Regulations for Lifting machinery

GB/T 3608   高处作业分级

GB/T 3608   Classification of high-altitude work

GB 30862    坠落防护挂点装置

GB 30862 	Fall protection anchor point device

GB 50194    建设工程施工现场供用电安全规范

GB 50194		Safety specifications for power supply and use at construction sites

GB 51210    建筑施工脚手架安全技术统一标准

GB 51210    Unified standard for Safety technology of scaffolding for building construction

GB 30871    危险化学品企业特殊作业安全规范

GB 30871    Safety Code for special operation of hazardous chemical enterprises

Q/SY 1236   高处作业安全管理规范 Code for Safety Management of work at heights

JGJ 46       施工现场临时用电安全技术规范

JGJ 46	Technical specification for safety of temporary electricity use at construction site

GB 2894     安全标志及其使用导则

GB 2894		Safety Signs and Use Guidelines

- 术语与定义 Terms and definitions

4.1高风险作业 High risk operation

一旦失去安全管控，可能导致人员群伤、死亡、环境重大污染或财产重大损失等的作业，通常被称为高风险作业。

Operations that may result in mass injury, death, major environmental pollution or major property losses if safety controls are lost are often referred to as high-risk operations.

4.2动火作业 Hot work

直接或间接产生明火的工艺设备以外的禁火区内可能产生火焰、火花或炽热表面的非常规作业，如使用电焊、气焊（割）、喷灯、电钻、砂轮、喷砂机等进行的作业。

Unconventional work that may produce flames, sparks, or hot surfaces in a no-fire zone other than process equipment that directly or indirectly produces open flames, such as work performed using electric welding, gas welding (cutting), blowtorch, drill, grinding wheel, sandblasting machine, etc.

4.3有限空间 Confined Space

有限空间是指进出口受限，通风不良，包括封闭、半封闭的设备、设施及场所，如反应器、塔、釜、槽、罐、炉膛、锅筒、管道以及地下室、窨井、坑（池）、下水道或其他封闭、半封闭场所。

Confined Space refers to the equipment, facilities and places with limited import and export and poor ventilation, including closed or semi-closed equipment, facilities and places, such as reactors, towers, reactors, tanks, tanks, furnaces, POTS, tubes, and basements, manholes, pits (pools), sewers or other closed or semi-closed places.

4.4 高处作业 High-altitude work

在距坠落基准面2m及2m以上有可能坠落的高处进行的作业。

Work performed at heights 2m or higher from the base level of fall where a fall is likely.
4.5吊装作业 Lifting operations

利用各种吊装机具将设备、工件、器具、材料等吊起，使其发生位置变化的作业。

The use of various lifting machines to lift equipment, workpieces, appliances, materials, etc., so that their position changes.

4.6临时用电 Temporary power supply

正式运行的电源上所接的非永久性用电。

Non-permanent power supply connected to a formal operating power source.
4.7动土作业 Excavation Work

挖土、打桩、钻探、坑探、地锚入土深度在0.5m以上；使用推土机、压路机等施工机械进行填土或平整场地等可能对地下隐蔽设施产生影响的作业。

Digging, piling, drilling, pit exploration, ground anchor depth of more than 0.5m; The use of bulldozers, road rollers and other construction machinery to fill the earth or level the site and other operations that may have an impact on underground concealed facilities.

- 职责 Responsibilities

  - EHS管理负责人 EHS officer

5.1.1 是高风险作业管理制度的归口部门。

It is the focal point of the high-risk operation management system.

5.1.1负责范围内高处作业、有限空间作业、动火作业、吊装作业、临时用电作业、开挖动土作业及其他高风险作业审批。

It is responsible for the approval of high-altitude operations, confined space operations, hot operations, lifting operations, temporary electricity operations, excavation and earth-moving operations and other high-risk operations within the scope.

- 程序 Procedures

  - 高风险作业范围 Scope of high risk operations

6.1.1包括动火作业、高处作业、临时用电作业、吊装作业、有限空间作业、动土作业。

Including hot work, high-altitude work, temporary electricity operation, confined space work, lifting operations, confined space operations, and earthwork.

  - 高风险作业审批 Approval of high risk operation

6.2.1 EHS管理负责人审批高风险作业，审批的人员，高风险作业审批人员应是专业工程技术人员或具有相关专业知识的人员。

The EHS officer shall specify the personnel responsible for the approval of high-risk operations, and the high-risk operations approval personnel should be professional engineering and technical personnel or personnel with relevant professional knowledge.

6.2.2 高风险作业审批人员应对高风险作业危险有害因素辨识情况和安全防范措施落实情况进行现场检查，并对现场操作作业人员的资格进行核实，确认可靠无误后，方可签发审批意见。

The approving personnel of high-risk operations shall conduct on-site inspection on the identification of dangerous and harmful factors and the implementation of safety precautions for high-risk operations, and verify the qualifications of on-site operation operators, and confirm that they are reliable and correct before issuing approval opinions.

6.2.3申请单位应对作业过程中的危险有害因素进行辨识、分析，包括准备过程、作业过程、作业后的整理或复位可能存在的危险有害因素，并针对存在的危险有害因素制定可靠的安全防范措施；检查现场操作作业人员的资格证书，并设置现场监护人员。

The applicant shall identify and analyze the hazardous and harmful factors in the process of operation, including the preparation process, operation process, post-operation arrangement or resetting of the possible hazardous and harmful factors, and formulate reliable safety preventive measures for the existing hazardous and harmful factors; Check the qualification certificates of on-site operation operators, and set up on-site guardianship personnel.

6.2.4外来施工单位实施高风险作业，由上海浦江数据中心相应的工程（项目）管理部门（单位）填写申请表，按照本制度要求办理审批手续。

When the external construction unit implements high-risk operations, the corresponding engineering (project) management department (unit) of SHANGHAI PUJIANG Data Center shall fill in the application form and go through the approval procedures in accordance with the requirements of this system.

  - 管理要求 Management requirements

6.3.1动火作业 Hot work

6.3.1.1涉及动火作业，应办理《动火作业许可证》，获得批准且现场按规范做好预防措施后，方可动火。

Involving hot work, should apply for the “hot work Permit”, approved and the site according to the norms to take preventive measures before fire.

6.3.1.2 动火作业须设置监护人，监护人可由二次施工管理员担任，监护人应了解动火区域或岗位存在的安全风险及管控措施，具备现场应急处置能力。

The fire operation must be set up a guardian, the guardian can be held by the secondary construction administrator, the guardian should understand the safety risks and control measures existing in the fire area or post, and have the ability to deal with emergencies on site.

6.3.1.3监护人应逐项检查防火措施落实情况。当发现动火作业人未持证上岗、动火部位与作业许可票（证）不相符或动火安全措施不落实时，监护人有权停止作业；当动火出现异常情况时应及时采取措施，有权中止作业；当动火人违章作业时，有权收回作业许可票（证）。

The guardian should check the implementation of fire prevention measures item by item. When it is found that the fire operator does not hold a certificate to work, the fire part is inconsistent with the work permit ticket (certificate) or the fire safety measures are not implemented, the guardian has the right to stop the operation; When the fire occurs abnormal situation should take timely measures, the right to suspend the operation; When the fire person violates the operation, he has the right to recover the operation permit ticket (certificate).

6.3.1.4	监护人在动火作业期间确需离开作业现场时，应收回动火人的动火许可票（证），暂停动火。动火作业前应清除动火现场及周围的易燃物品，或采取其他有效安全防火措施，并配备消防器材，满足作业现场应急需求。

When the guardian really needs to leave the work site during the hot work period, he shall take back the hot work permit ticket (certificate) and suspend the hot work.Before the fire operation, the inflammable articles in and around the fire site should be removed, or other effective safety and fire prevention measures should be taken, and fire fighting equipment should be equipped to meet the emergency needs of the work site.

6.3.1.5 动火点周围或其下方如有可燃物、电缆桥架、空洞、窨井、地沟、水封设施等，应检查分析并采取清理或封盖等措施；对于动火点周围30m内有可能泄漏易燃、可燃物料的设施，应采取隔离措施。

If there are combustibles, cable Bridges, voiding, manholes, trenches and water sealing facilities around or below the hot spot, check and analysis should be taken and measures such as cleaning or capping should be taken; For the facilities that may leak flammable and combustible materials within 30m around the ignition point, isolation measures should be taken.

6.3.1.6凡在盛有或盛装过易燃易爆危险化学品的设备、管道等生产、储存设施及甲、乙类区域的生产设备上的动火作业，应将上述设备设施与生产系统彻底隔离，并进行清洗、置换，分析合格后方可作业。严禁以水封或关闭阀门代替盲板作为隔断措施。因条件限制无法进行清洗、置换而确需动火作业时按特级动火作业规定执行，对无法用盲板隔离的大口径管道上的动火应对作业风险及防范措施进行充分论证，按特级动火作业规定执行。

Where there are or contain inflammable and explosive dangerous chemicals equipment, pipelines and other production, storage facilities and production equipment in class A and B areas of the fire operation, the above equipment and facilities should be completely isolated from the production system, and cleaning, replacement, analysis of qualified before operation. It is strictly prohibited to use water seal or close valve instead of blind plate as a partition measure. When cleaning and replacement cannot be carried out due to conditions and it is necessary to perform hot work according to the provisions of special class hot work, fully demonstrate the risks and preventive measures of hot work on large diameter pipelines that cannot be isolated by blind plates, and perform according to the provisions of special class hot work.

6.3.1.7拆除管线进行动火作业时，应先查明其内部介质及其走向，并根据所要拆除管线的情况制订安全防护措施。

When removing the pipeline for fire operation, the internal medium and its direction should be identified first, and safety protection measures should be formulated according to the situation of the pipeline to be removed.

6.3.1.8在有可燃物构件和使用可燃物做防腐内衬的设备内部进行动火作业时，应采取防火隔绝措施。

When there are combustible components and the use of combustible materials as anti-corrosion lining of the equipment for fire operation, fire isolation measures should be taken.

6.3.1.9存在受热后可能释放出有害物质材料的设备内部，未采取有效隔绝及防护措施时，严禁动火。

When there are harmful materials that may be released after heating inside the equipment, no effective isolation and protective measures are taken, it is strictly prohibited to start fire.

6.3.1.10作业过程中可能释放出易燃易爆物质的设备上，未采取有效防范措施时，严禁动火。

When flammable and explosive materials may be released in the course of operation, it is strictly prohibited to start fire without taking effective preventive measures.

6.3.1.11在生产、使用、储存氧气的设备上进行动火作业时，设备内氧含量不应超过23.5%。

In the production, use, storage of oxygen equipment for hot work, the oxygen content in the equipment should not exceed 23.5%.

6.3.1.12动火期间，距动火点30m内不应排放可燃气体；距动火点15m内不应排放可燃液体；在动火点15m范围内、动火点上方及下方不应同时进行可燃溶剂清洗或喷漆等作业。

Combustible gas should not be discharged within 30m from the ignition point during the hot fire period; Combustible liquid should not be discharged within 15m from the ignition point; In the range of 15m of the ignition point, above and below the ignition point should not be carried out at the same time, such as flammable solvent cleaning or painting operations.

6.3.1.12使用气焊、气割动火作业时，乙炔瓶应直立放置，氧气瓶与乙炔瓶的间距不应小于5m，二者与作业地点间距不应小于10m，并应设置防晒设施与防倾倒措施。

When using gas welding and gas cutting, the acetylene cylinder should be placed upright, the distance between the oxygen cylinder and the acetylene cylinder should not be less than 5m, the distance between the two and the working site should not be less than 10m, and the sun protection facilities and anti-dumping measures should be set.

6.3.1.13作业完毕后应清理现场，确认无残留火种后方可离开。

After the operation is finished, the site should be cleaned up and no residual flame can be left.

6.3.1.14遇五级风以上（含五级）天气，原则上禁止露天动火作业；因生产确需动火，动火作业应升级管理。

In case of level 5 wind or above (including level 5) weather, in principle, open fire operation is prohibited; Because the production really needs to be hot, hot operation should be upgraded management.

6.3.1.15使用电焊机作业时，电焊机不应放置在运行的生产装置、罐区和具有火灾爆炸危险场所内，否则按照动火作业的要求进行动火分析。

When the welding machine is used, the welding machine should not be placed in the operating production equipment, tank farm and places with fire and explosion hazards, otherwise the hot fire analysis should be carried out in accordance with the requirements of hot fire operation.

6.3.1.16特级动火作业在符合上述规定的同时，还应符合以下规定：

Special hot operation in accordance with the above provisions at the same time, should also meet the following provisions:

- 应预先制定作业方案，落实安全防火措施，必要时可请专职消防队在现场监护；动火点所在的楼栋应预先通知单位生产协调、组织部门及其它相关部门，使之在异常情况下能及时采取相应的应急措施；应在正压条件下进行作业。

The operation plan should be formulated in advance, the safety and fire prevention measures should be implemented, and the full-time fire brigade can be asked to monitor the scene if necessary; The building where the fire point is located should notify the unit production coordination, organization department and other relevant departments in advance, so that it can take corresponding emergency measures in a timely manner under abnormal circumstances; Work should be carried out under positive pressure conditions.

- 应保持作业现场通排风良好。

The working site should be kept in good ventilation.

- 动火现场应配置便携式或移动式可燃气体检测报警仪，连续监测动火作业点周围可燃气体浓度，发现可燃气体浓度超限报警，须立即停止作业。

Portable or mobile combustible gas detection and alarm instrument should be installed in the hot fire site to continuously monitor the combustible gas concentration around the hot fire operation point. If the combustible gas concentration exceeds the limit, the alarm should be given, and the operation should be stopped immediately.

- 根据动火作业的分级管理，动火许可证的有效期，见表1：

According to the graded management of hot operation, the validity period of hot fire license is shown in Table 1:

表1 动火作业分级

Table 1 Classification of hot work

| 序号 No. | 区域 Aera | 动火作业分级 Classification | 动火许可证 有效期 Expiration date |
| --- | --- | --- | --- |
| 1 | 日用油间、带载模块机房、核心网络机房/运营商接入间、柴油发电房、地埋油罐、厨房区域（使用液化气或天然气） Daily oil room, on-load module room, core network room/operator access room, diesel power generation room, buried oil tank, kitchen area (using LPG or natural gas) | 特级动火 Special level | 不超过8 小时 No more than 8 hrs |
| 2 | 配电房、变配电室、电池间、库房、无负载模块机房、办公室、风机房、强弱电间、管道井、线缆井、冷冻站、冷却塔、消防水泵房、柴发雨淋间、气灭钢瓶间 Power distribution room, transformer and distribution room, battery room, warehouse, no load module room, office, wind room, strong and weak power room, pipeline well, cable well, freezing station, cooling tower, fire pump room, firewood rain shower room, gas cylinder room | 一级动火 Level I | 不超过8 小时 No more than 8 hrs |
| 3 | 室外供应商临时办公、预支场地、建筑外动火、厨房区域（使用电加热） Outdoor vendor temporary office, advance space, hot fire outside building, kitchen area (use electric heating) | 二级动火 Level II | 不超过72 小时 No more than 72hrs |

6.3.1.17 遇节假日、公休日、夜间或其他特殊情况，动火作业应提级管理。

In case of holidays, public holidays, night or other special circumstances, hot work should be upgraded management.

6.3.2高处作业 High-altitude work

6.3.2.1在进行高处作业前需申请《高处作业许可证》，且作业人员需持有特种作业许可证，方可作业。

Before carrying out high work, it is necessary to apply for " Work-at-Height Permit ", and the operator must hold a special work permit before operating.

6.3.2.2《高处作业许可证》有效期最长为7天。

The Permit for work-at-height is valid for up to 7 days.

6.3.2.3凡患高血压、心脏病、贫血病、癫痫病、精神病以及其他不适合高处作业疾患的人员，不得从事高处作业。

Persons suffering from high blood pressure, heart disease, anemia, epilepsy, mental illness and other diseases unsuitable for working at heights shall not engage in work at heights.

6.3.2.4作业人员应正确配戴符合要求的安全带。带电高处作业应使用绝缘工具或穿均压服。Ⅳ级高处作业（30m以上）宜配备通讯联络工具。

The operators shall correctly wear safety belts that meet the requirements. Insulated tools or uniform should be used when working at high places with electricity. ⅳ-level high work (30m or more) should be equipped with communication tools.

6.3.2.5高处作业应设专人监护，作业监护人应承担以下职责：

The high work should be supervised by special personnel, and the operation guardian should bear the following responsibilities:

- 了解作业区域或岗位的周边环境和风险，熟悉应对突发事件的处置程序。

Understand the surrounding environment and risks of the work area or post, and be familiar with the disposal procedures for emergencies.

- 作业监护人在作业前，负责对安全措施落实情况进行检查，发现安全措施不落实或不完善时，应制止作业。

The operation guardian shall be responsible for checking the implementation of safety measures before operation, and shall stop the operation if it is found that safety measures are not implemented or incomplete.

- 当发现高处作业内容与安全作业票（证）不相符，或者相关安全措施不落实时，应制止作业。

When it is found that the content of the operation at the height is inconsistent with the safety operation ticket (certificate), or the relevant safety measures are not implemented, the operation should be stopped.

- 作业过程中出现异常时，应及时采取措施，终止作业。

When there is an anomaly in the process of operation, measures should be taken in time to terminate the operation.

- 作业过程中，监护人不得随意离开现场，确需离开时，收回安全作业票（证）。

During the operation, the guardian shall not leave the site at will. When it is necessary to leave, the safety operation ticket (certificate) shall be withdrawn.

- 暂停作业。

Suspend the operation.

6.3.2.6脚手架的搭设应符合《建筑施工脚手架安全技术统一标准》（GB 51210）、《起重机械安全规程》（GB6067）等国家有关标准，并经过验收合格、悬挂合格标识牌后方可使用。

The erection of scaffolding should conform to the "Unified Standard of Safety Technology for Construction Scaffolding" (GB 51210), "Safety Regulations for Lifting Machinery" (GB6067) and other relevant national standards, and can be used after acceptance and hanging qualified identification plates.

6.3.2.7在彩钢板屋顶、石棉瓦、瓦棱板等轻型材料上作业，应铺设牢固的脚手板并加以固定，脚手板上要有防滑措施。

In the color steel plate roof, asbestos tile, tile edge plate and other light materials, should be laid firmly and fixed, the foot and hand plate should have anti-slip measures.

6.3.2.8雨天和雪天作业时，应采取可靠的防滑、防寒措施；遇有五级以上强风、浓雾等恶劣气候，不应进行高处作业、露天攀登与悬空高处作业；暴风雪、台风、暴雨后，应对作业安全设施进行检查，发现问题立即处理。

When working on rainy and snowy days, reliable anti-slip and cold-proof measures should be taken; In case of strong wind above grade 5, thick fog and other bad weather, should not carry out high work, open-air climbing and suspended high work; After blizzards, typhoons and rainstorms, work safety facilities should be checked, and problems should be dealt with immediately.

6.3.2.9作业过程中使用的工具、材料、零件等应装入工具袋，上下架板时手中不应持物，不应投掷工具、材料及其他物品。易滑动、易滚动的工具、材料堆放在脚手架上时，应采取防坠落措施。

Tools, materials, parts, etc. used in the process of operation should be put into the tool bag, the hand should not hold objects, should not throw tools, materials and other objects. When the tools and materials that are easy to slide and roll are stacked on the scaffold, anti-fall measures should be taken.

6.3.2.10与其他作业交叉进行时，应按指定的路线上下，不应上下垂直作业，如果确需垂直作业应采取可靠的隔离措施。

When crossing with other operations, they should go up and down according to the designated route, and should not work vertically up and down. If vertical work is necessary, reliable isolation measures should be taken.

6.3.3吊装作业Lifting operation

6.3.3.1吊装作业指使用桥式起重机、门式起重机、塔式起重机、汽车吊、升降机等起吊设备将重物吊起，并使重物发生位置变化的作业。施工方在园区内进行吊装作业时需申请《吊装作业许可证》，有效期最长7天。

Lifting operation refers to the use of bridge cranes, gantry cranes, tower cranes, car cranes, lifts and other lifting equipment to lift heavy objects, and make heavy objects change position. When carrying out lifting operations in the park, the construction party shall apply for the Lifting Operation Permit, which is valid for a maximum of 7 days.

6.3.3.2一级（起吊物重量＞100t）、二级吊装作业(40t≤起重物重量≤100t)，应编制吊装作业方案。吊装物体质量虽不足40t，但形状复杂、刚度小、长径比大、精密贵重，以及在作业条件特殊的情况下，三级吊装作业(起重物重量＜40t)也应编制吊装作业方案，吊装作业方案应经审批。

For the first level (lifting weight > 100t) and the second level lifting operation (40t≤ lifting weight ≤100t), the hoisting operation plan should be prepared. Although the weight of the lifting object is less than 40t, the shape is complex, the rigidity is small, the ratio of length to diameter is large, the precision is valuable, and in the case of special working conditions, the lifting operation plan should also be prepared for the three-level lifting operation (lifting weight < 40t), and the lifting operation plan should be approved.

6.3.3.3吊装现场应设置安全警戒标志，非作业人员禁止进入作业警戒范围，安全警戒标志应符合《安全标志及其使用导则》（GB2894） 的规定。

Safety warning signs should be set up at the hoisting site, non-operators are prohibited from entering the scope of operation warning, safety warning signs should comply with the provisions of the "Safety signs and Guidelines for their Use" (GB2894).

6.3.3.4吊装现场应设专人监护，作业监护人应承担以下职责：

The hoisting site should be supervised by special personnel, and the operation guardian should bear the following responsibilities:

- 确保吊装过程中警戒范围内没有非作业人员或车辆经过。

Ensure that no non-operator or vehicle passes within the warning range during the hoisting process.

- 吊装作业过程中不得擅自离开现场，按规定落实吊装作业安全措施，保证在作业过程中始终具备安全作业条件。

It is not allowed to leave the site without authorization during the lifting operation, and the safety measures for the lifting operation shall be implemented according to the regulations to ensure that safe working conditions are always available during the operation.

- 当发现吊装作业内容与安全作业票（证）不相符，或者相关安全措施不落实时，应制止作业。

When it is found that the content of lifting operation is inconsistent with the safety operation ticket (certificate), or the relevant safety measures are not implemented, the operation should be stopped.

- 作业过程中出现异常时，应及时采取措施，终止作业。

When there is an anomaly in the operation process, measures should be taken in time to terminate the operation.

6.3.3.5不应靠近输电线路进行吊装作业。确需在输电线路附近作业时，起重机械的安全距离应大于起重机械的倒塌半径的要求；不能满足时，应停电后再进行作业。吊装场所如有含危险物料的设备、管道等时，应制定详细吊装方案，并对设备、管道采取有效防护措施，必要时停车，放空物料，置换后进行吊装作业。

The lifting operation should not be carried out near the transmission line. When it is necessary to operate near the transmission line, the safety distance of the lifting machinery should be greater than the requirements of the collapse radius of the lifting machinery; If it cannot be met, the operation should be carried out after the power failure. If there are equipment and pipelines containing dangerous materials in the lifting site, a detailed lifting plan should be formulated, and effective protective measures should be taken for the equipment and pipelines. If necessary, stop the vehicle, empty the materials, and carry out the lifting operation after replacement.

6.3.3.6大雪、暴雨、大雾及六级以上大风时，不应露天作业。

When there is heavy snow, heavy rain, heavy fog and strong wind above six level, it should not be operated in the open air.

6.3.3.7作业前，作业单位应对起重机械、吊具、索具、安全装置等进行检查，确保其处于完好状态。

Before the operation, the operation unit should check the lifting machinery, slings, rigging, safety devices, etc., to ensure that they are in good condition.

6.3.3.8应按规定负荷进行吊装，吊具、索具应经计算选择使用，不应超负荷吊装。

The lifting should be carried out according to the specified load, and the lifting gear and rigging should be selected and used after calculation, and should not be overloaded.

6.3.3.9不应利用管道、管架、电杆、机电设备等作吊装锚点。未经土建专业审查核算，不应将建筑物、构筑物作为锚点。

Should not use pipe, pipe frame, electric pole, mechanical and electrical equipment as hoisting anchor point. Buildings and structures should not be used as anchor points without civil engineering professional review and accounting.

6.3.3.10起吊前应进行试吊，试吊中检查全部机具、地锚受力情况，发现问题应将吊物放回地面，排除故障后重新试吊，确认正常后方可正式吊装。

Test lifting should be carried out before lifting. During the test lifting, check the loading condition of all tools and ground anchors. If any problem is found, the suspended objects should be put back to the ground.

6.3.3.11指挥人员应佩戴明显的标志，并按规定的联络信号进行指挥。

The commanding personnel should wear obvious signs and conduct command according to the specified contact signal.

6.3.3.12 起重机械操作人员应遵守如下规定：

Lifting machinery operators should comply with the following provisions:

- 按指挥人员发出的指挥信号进行操作。

Operate according to the command signal issued by the command personnel.

- 任何人发出的紧急停车信号均应立即执行。

Any emergency stop signal issued by anyone should be acted upon immediately.

- 吊装过程中出现故障，应立即向指挥人员报告。

If there is a malfunction during hoisting, it should be reported to the command personnel immediately.

- 重物接近或达到额定起重吊装能力时，应检查制动器，用低高度、短行程试吊后，再吊起。

When the heavy object approaches or reaches the rated lifting capacity, the brake should be checked, and after a low height and short stroke test lifting, it should be lifted.

- 利用两台或多台起重机械吊运同一重物时应保持同步，各台起重机械所承受的载荷不应超过各自额定起重能力的80％。

The use of two or more lifting machinery to lift the same heavy object should be kept synchronized, the load borne by each lifting machinery should not exceed 80% of their rated lifting capacity.

- 下放吊物时，不应自由下落（溜），不应利用极限位置限制器停车。

When lowering the lifting, it should not be free to fall (slip), and should not use the limit position limiter to stop.

- 不应在起重机械工作时对其进行检修；不应在有载荷的情况下调整起升变幅机构的制动器。

It should not be overhauled when the lifting machinery is working; The brake of the lifting mechanism should not be adjusted under load.

- 停工和休息时，不应将吊物、吊笼、吊具和吊索悬在空中。

Suspensions, cages, spreaders and slings should not be suspended in the air during downtime and rest.

- 以下情况不应起吊：The following should not be hoisted:

——无法看清场地、吊物，指挥信号不明。

Unable to see the site, lifting objects, command signals unknown.

——起重臂吊钩或吊物下面有人、吊物上有人或浮置物。

There is someone under the boom hook or hanging object, someone on the  hanging object or floating object.

——重物捆绑、紧固、吊挂不牢，吊挂不平衡，绳打结，绳不齐，斜拉重物，棱角吊物与钢丝绳之间没有衬垫。

Heavy objects binding, fastening, hanging is not firmly, hanging is not balanced, rope knotting, rope uneven, diagonal heavy objects, there is no liner between the angular lifting object and the wire rope.

——重物质量不明，与其他重物相连，埋在地下，与其他物体冻结在一起。

The weight is of unknown quality, connected to other weights, buried in the ground, and frozen with other objects.

- 听从指挥人员的指挥，并及时报告险情。

Follow the command of the commanding staff, and report the danger in time.

6.3.3.13应用吊钩直接缠绕重物及将不同种类或不同规格的索具混在一起使用。

Use hooks to wrap heavy objects directly and mix different types or different specifications of rigging together.

6.3.3.14吊物捆绑应牢靠，吊点和吊物的重心应在同一垂直线上；起升吊物时应检查其连接点是否牢固、可靠；吊运零散件时，应使用专门的吊篮、吊斗等器具，吊篮、吊斗等不应装满。

The lifting should be firmly bound, and the lifting point and the center of gravity of the lifting should be on the same vertical line; When lifting the lifting object, check whether its connection point is firm and reliable; When lifting scattered pieces, special hanging baskets, hanging buckets and other equipment should be used, and hanging baskets, hanging buckets and other equipment should not be filled.

6.3.3.15起吊重物就位时，应与吊物保持一定的安全距离，用拉伸或撑杆、钩子辅助其就位起吊重物就位前，不应解开吊装索具；与司索人员有关的不应起吊的情况，司索工应做相应处理。

When lifting heavy objects in place, should keep a certain safe distance from the lifting objects, with stretching or support rod, hook to assist its position before lifting heavy objects in place, should not untie the lifting rigging; Related to the cable personnel should not lift the situation, cable workers should do the corresponding treatment.

6.3.3.16用定型起重机械（例如履带吊车、轮胎吊车、桥式吊车等）进行吊装作业时，除遵守本标准外，还应遵守该定型起重机械的操作规程。

When using stereotyped lifting machinery (such as crawler crane, tire crane, bridge crane, etc.) to carry out lifting operations, in addition to complying with this standard, the operating rules of the stereotyped lifting machinery should be observed.

6.3.3.17作业完毕应做如下工作：

The following work should be done after completion of the operation:

将起重臂和吊钩收放到规定位置，所有控制手柄均应放到零位，电气控制的起重机械的电源开关应断开。

The lifting arm and hook should be put into the specified position, all control handles should be placed in zero position, and the power switch of the electrically controlled lifting machinery should be disconnected.

6.3.3.18对在轨道上作业的吊车，应将吊车停放在指定位置有效锚定。

For cranes operating on the track, the crane should be parked in the designated position for effective anchoring.

6.3.3.19 吊索、吊具应收回，放置到规定位置，并对其进行例行检查。

The slings and spares should be recovered, placed in the specified position, and routinely inspected.

6.3.4有限空间作业 Confined Space operation

6.3.4.1作业单位（数据中心、客户、承包商、供应商等相关方）必须办理《有限空间作业许可证》，按国家安全规范做好防护措施后，方可进行有限空间作业。《有限空间作业许可证》有效期不超过24小时。

The operation unit (data center, customer, contractor, supplier and other relevant parties) must apply for the Confined Space Operation License  and take protective measures according to the national security norms before carrying out confined space operation. The validity period of the Confined Space Operation License shall not exceed 24 hours.

6.3.4.2 EHS管理负责人应当对有限空间进行辨识，建立《上海浦江数据中心有限空间台账》（附件7），明确有限空间数量、位置以及危险因素等信息，并及时更新。

The person in charge of EHS management shall identify the confined space, establish the Confined Space Log of SHANGHAI PUJIANG Data Center (Attachment 7), clarify the confined space quantity, location, risk factors and other information, and update it in time.

6.3.4.3有限空间出入口等醒目位置设置明显的安全警示标志，并在具备条件的场所设置安全风险告知牌。

Obvious safety warning signs shall be set up at the entrance and exit of confined space and other eye-catching locations, and safety risk warning boards shall be set up in places where conditions are met.

6.3.4.4应对有限空间进行安全隔绝，要求如下：

Confined space should be safely isolated, and the requirements are as follows:

- 有限空间内的用电设备应停止运行并切断电源，在电源开关处上锁并加挂警示牌。

The electrical equipment in the confined space should stop running and cut off the power supply, lock the power switch and put up a warning sign.

- 与有限空间连通的可能危及安全作业的孔、洞应进行严密封堵。

Holes and holes connected with the confined space that may endanger safe operation should be tightly sealed.

6.3.4.5作业前，应根据有限空间盛装（过）的物料特性，对有限空间进行清洗或置换，并对有限空间进行气体检测，检测内容及达到要求如下：

Before operation, the confined space should be cleaned or replaced according to the material characteristics of the confined space containing (over), and the confined space should be detected by gas. The detection content and the requirements are as follows:

a) 氧含量为19.5%～21%，在富氧环境下不应大于23.5%。

The oxygen content is 19.5% ~ 21%, which should not be greater than 23.5% in the oxygen-rich environment.

b) 有毒物质为0，可燃气体、蒸气允许浓度不大于0.2%（体积分数）。

Toxic substances are 0, and the allowable concentration of combustible gas and vapor is not more than 0.2% (volume fraction).

6.3.4.6应保持有限空间空气流通良好，可采取如下措施：

Good air circulation should be maintained in the confined space, and the following measures can be taken:

- 打开人孔、手孔、料孔、风门、烟门等与大气相通的设施进行自然通风；

Open manhole, hand hole, material hole, damper, smoke door and other facilities connected with the atmosphere for natural ventilation;

- 必要时，应采用风机强制通风或管道送风，管道送风前应对管道内介质和风源进行分析确认。

If necessary, fan forced ventilation or pipeline air supply should be used, and the media and wind source in the pipeline should be analyzed and confirmed before pipeline air supply.

6.3.4.7 应对有限空间内的气体浓度进行严格监测，监测要求如下：

The gas concentration in the confined space should be strictly monitored, and the monitoring requirements are as follows:

- 作业前30min内，应对有限空间进行气体分析，分析合格后方可进入。

Within 30 minutes before the operation, the gas analysis should be carried out in the confined space, and the analysis can only be entered after passing the test.

- 监测点应有代表性，容积较大的有限空间，应对上、中、下各部位进行监测分析。

The monitoring point should be representative and confined space with large volume, and the upper, middle and lower parts should be monitored and analyzed.

- 分析仪器应在校验有效期内，使用前应保证其处于正常工作状态。

The analytical instrument should be in the validity period of calibration, and it should be ensured that it is in normal working condition before use.

- 监测人员进入或探入有限空间监测时应采取有效的个体防护措施。

The monitoring personnel shall take effective personal protective measures when entering or probing the confined space for monitoring.

- 作业现场应配置便携式或移动式气体检测报警仪，连续监测有限空间内氧气、可燃气体、蒸气和有毒气体浓度，发现气体浓度超限报警，应立即停止作业、撤离人员、对现场进行处理，并分析合格后方可恢复作业。

The work site shall be equipped with portable or mobile gas detection and alarm instrument to continuously monitor the concentration of oxygen, combustible gas, vapor and toxic gas in the confined space. If the gas concentration exceeds the limit, the alarm shall be given. The operation shall be stopped immediately, the personnel shall be evacuated, the site shall be treated, and the operation can be resumed after the analysis is qualified.

- 涂刷具有挥发性溶剂的涂料时，应采取强制通风措施。

When coating with volatile solvent, forced ventilation measures should be taken.

- 作业中断时间超过60min时，应重新进行分析。

When the operation is interrupted for more than 60 minutes, the analysis should be re-performed.

6.3.4.8当一处有限空间内存在动火作业时，该处有限空间内严禁安排涂刷等其他作业活动。

When there is hot work in a confined space, it is strictly prohibited to arrange other operation activities such as painting in the confined space.

6.3.4.9进入有限空间作业人员应按规定着装并正确佩戴相应的个体防护用品；进入下列有限空间作业应采取如下防护措施：

Workers entering the confined space should dress in accordance with regulations and properly wear the corresponding personal protective equipment; The following protective measures should be taken when entering the following confined space operations:

- 缺氧或有毒的有限空间经清洗或置换仍达不到要求的，应佩戴隔绝式呼吸防护装备，并应拴带救生绳。

Hypoxic or toxic confined space after cleaning or replacement still can not meet the requirements, should wear isolation respiratory protective equipment, and should be tied with life rope.

- 易燃易爆的有限空间经清洗或置换仍达不到要求的，应穿防静电工作服及防静电工作鞋，使用防爆型低压灯具及防爆工具。

Flammable and explosive confined space after cleaning or replacement still can not meet the requirements, should wear anti-static work clothes and anti-static shoes, the use of explosion-proof low-voltage lamps and explosion-proof tools.

- 电焊作业，应穿戴绝缘鞋。

For electric welding operations, insulated shoes should be worn.

- 进入有噪声产生的有限空间，应配戴耳塞或耳罩等防噪声护具。

Wear anti-noise protection such as earplugs or earmuffs when entering a confined space with noise.

- 进入有粉尘产生的有限空间，应配戴防尘口罩、眼罩等防尘护具。

Dust masks, eye masks and other dust protective gear should be worn when entering a confined space with dust production.

- 进入高温的有限空间作业时，应穿戴高温防护用品，必要时采取通风、隔热、佩戴通讯设备等防护措施。

When working in a confined space with high temperature, wear high temperature protective equipment, and take protective measures such as ventilation, heat insulation and communication equipment if necessary.

- 进入低温的有限空间作业时，应穿戴低温防护用品，必要时采取供暖、佩戴通讯设备等措施。

When working in a low-temperature confined space, you should wear low-temperature protective equipment, and take measures such as heating and communication equipment when necessary.

- 在有限空间内从事清污作业，应佩戴隔绝式呼吸防护装备，并应拴带救生绳。

In the confined space engaged in cleaning operations, should wear isolated respiratory protective equipment, and should be tied with a safety rope.

6.3.4.10照明及用电安全要求如下：

Lighting and electricity safety requirements are as follows:

- 有限空间照明电压应小于等于36V，在潮湿容器、狭小容器内作业电压应小于等于12V。

Confined space lighting voltage should be less than or equal to 36V, in wet containers, small containers operating voltage should be less than or equal to 12V.

- 在潮湿容器中，作业人员应站在绝缘板上，同时保证金属容器接地可靠。

In the wet container, the operator should stand on the insulation board, while ensuring that the metal container is grounded reliably.

6.3.4.11在有限空间外应设有专人监护，作业监护人应承担以下职责：

There should be a special person to monitor outside the confined space, and the operation guardian should bear the following responsibilities:

- 作业监护人应熟悉作业区域的环境和风险情况，有判断和处理异常情况的能力，掌握急救知识。

The operation guardian should be familiar with the environment and risk situation of the operation area, can judge and deal with abnormal situations, and master first aid knowledge.

- 作业监护人在作业人员进入有限空间作业前，负责对安全措施落实情况进行检查，发现安全措施不落实或不完善时，应制止作业。

The operation guardian shall be responsible for checking the implementation of safety measures before the operation personnel enter the confined space. If the safety measures are not implemented or incomplete, the operation shall be stopped.

- 作业监护人应清点出入有限空间的作业人数，在出入口处保持与作业人员的联系，当发现异常情况时，应及时制止作业，并立即采取救护措施。

The operation guardian shall count the number of operators entering and leaving the confined space, keep in touch with the operators at the exit entrance, and stop the operation in time when any abnormal situation is found, and immediately take rescue measures.

- 在风险较大的有限空间作业时，应增设监护人员。

When operating in a confined space with greater risk, additional guardianship personnel should be added.

- 作业过程中必须实行全过程监护，作业监护人在作业期间，不得离开作业现场或做与监护无关的事。

During the operation, the whole process of supervision must be implemented, and the operation guardian shall not leave the operation site or do anything unrelated to the supervision during the operation.

6.3.4.12 应满足的其他要求如下：

Other requirements that should be met are as follows:

- 有限空间外应设置安全警示标志，备有隔绝式呼吸防护装备、消防器材和清水等相应的应急器材及用品。

Safety warning signs should be set up outside the confined space, and corresponding emergency equipment and supplies such as isolated respiratory protective equipment, fire fighting equipment and water should be available

- 有限空间出入口应保持畅通。

The entrance and exit of the confined space should be kept unblocked.

- 作业前后应清点作业人员和作业工器具。

Personnel and equipment should be counted before and after the operation.

- 作业人员不应携带与作业无关的物品进入有限空间。

Operators should not carry items unrelated to the operation into the confined space.

- 作业中不应抛掷材料、工器具等物品。

Materials, tools and other items should not be thrown during the operation.

- 在有毒、缺氧环境下不应摘下防护面具。

Protective masks should not be removed in toxic and hypoxic environments.

- 不应向有限空间充氧气或富氧空气。

Oxygenated or oxygen-enriched air should not be filled into confined Spaces.

- 离开有限空间时应将气割（焊）工器具带出。

Gas cutting (welding) equipment should be taken out when leaving the confined space.

- 难度大、劳动强度大、时间长、高温的有限空间作业应采取轮换作业方式。

The confined space operation with high difficulty, high labor intensity, long time and high temperature should take rotation mode of operation.

- 作业结束后，有限空间所在单位和作业单位共同检查有限空间内外，确认无问题后方可封闭有限空间。

After the completion of the operation, the unit where the confined space is located and the operating unit shall jointly check the inside and outside of the confined space and confirm that there is no problem before closing the confined space.

- 作业期间发生异常情况时，严禁无防护救援。

When any abnormal situation occurs during the operation, it is strictly prohibited to rescue without protection.

- 有限空间作业停工期间，应增设警示标志，并采取防止人员误入的措施。

During the period of work stoppage in confined space, warning signs should be added and measures should be taken to prevent personnel from straying.

- 使用便携式、移动式可燃气体检测报警仪或其他类似手段进行分析时，气体检测报警仪应按有关规定进行检测合格方可使用，特殊情况需要进行标准气浓度标定。

When portable or mobile combustible gas detection and alarm instrument or other similar means are used for analysis, the gas detection and alarm instrument shall be tested according to relevant regulations before being used. In special cases, standard gas concentration calibration is required.

    - 临时用电作业 Temporary power supply

      - 作业单位（数据中心、客户、承包商、供应商等相关方）作业前必须办理《临时用电许可证》，按国家安全规范做好防护措施后，方可按照现场指定电源使用。有效期不超过7天。

#### The operation unit (data center, customers, contractors, suppliers and other relevant parties) must apply for the Temporary Electricity License before operation, and take protective measures according to the national safety norms before using the designated power supply on site. The validity period shall not exceed 7 days.

      - 在运行的生产装置、罐区和具有火灾爆炸危险场所内不应接临时电源，确需时应对周围环境进行可燃气体检测分析，分析结果应符合规定要求。

#### Temporary power supply should not be connected in the operating production units, tank farms and places with fire and explosion hazards. Flammable gas detection and analysis should be carried out in the surrounding environment when necessary, and the analysis results should meet the prescribed requirements.

      - 各类移动电源及外部自备电源，不应接入电网。

#### All kinds of mobile power supplies and external self-provided power supplies should not be connected to the power grid.

      - 动力和照明线路应分路设置。

#### Power and lighting lines should be set separately.

      - 在开关上接引、拆除临时用电线路时，其上级开关应断电并加挂安全警示标牌。

#### When connecting and removing temporary power lines on the switch, its upper switch should be powered off and safety warning signs should be attached.

      - 临时用电应设置保护开关，使用前应检查电气装置和保护设施的可靠性。所有的临时用电均应设置接地保护。

#### Protection switch should be set for temporary power consumption, and the reliability of electrical equipment and protection facilities should be checked before use. Grounding protection should be set up for all temporary electricity use.

      - 临时用电设备和线路应按供电电压等级和容量正确使用，所用的电器元件应符合国家相关产品标准及作业现场环境要求，临时用电电源施工、安装应符合  《施工现场临时用电安全技术规范》（JGJ 46）的有关要求，并有良好的接地，临时用电还应满足如下要求：

#### Temporary electrical equipment and lines should be used correctly according to the power supply voltage level and capacity, the electrical components used should meet the relevant national product standards and the environmental requirements of the work site, the construction and installation of temporary power supply should meet the relevant requirements of the "construction site temporary electricity safety Technical Specifications" (JGJ 46), and have good grounding, temporary electricity should also meet the following requirements:

- 火灾爆炸危险场所应使用相应防爆等级的电源及电气元件，并采取相应的防爆安全措施。

Fire and explosion danger places should use the corresponding explosion-proof grade of power supply and electrical components, and take the corresponding explosion-proof safety measures.

- 临时用电线路及设备应有良好的绝缘，所有的临时用电线路应采用耐压等级不低于500V 的绝缘导线。

Temporary power lines and equipment should be well insulated, and all temporary power lines should use insulated wires with a voltage rating of not less than 500V.

- 临时用电线路经过有高温、振动、腐蚀、积水及产生机械损伤等区域，不应有接头，并应采取相应的保护措施。

Temporary power lines through high temperature, vibration, corrosion, water and mechanical damage and other areas, there should be no joint, and should take appropriate protective measures.

      - 临时用电架空线应采用绝缘铜芯线，并应架设在专用电杆或支架上。其最大弧垂与地面距离，在作业现场不低于2.5m，穿越机动车道不低于5m。

#### Temporary electric overhead lines should be insulated copper core wires, and should be erected on special poles or supports. The maximum sag distance from the ground shall be not less than 2.5m at the job site and not less than 5m across the motor vehicle road.

      - 对需埋地敷设的电缆线路应设有走向标志和安全标志。电缆埋地深度不应小于0.7m，穿越道路时应加设防护套管。

#### The cable lines to be laid in the ground shall be provided with direction signs and safety signs. The depth of the cable buried should not be less than 0.7m, and the protective sleeve should be installed when crossing the road.

      - 现场临时用电配电盘、箱应有电压标识和危险标识，应有防雨措施，盘、箱、门应能牢靠关闭并上锁管理。

#### The temporary power distribution board and box should be marked with voltage and danger, and should have rainproof measures. The panel, box and door should be securely closed and locked for management.

      - 行灯电压不应超过36V；在特别潮湿的场所或塔、釜、槽、罐等金属设备内作业，临时照明行灯电压不应超过12V。

#### The lamp voltage should not exceed 36V; In particularly humid places or towers, tanks, tanks and other metal equipment, temporary lighting line lamp voltage should not exceed 12V.

      - 临时用电设施应安装符合规范要求的漏电保护器，移动工具、手持式电动工具应逐个配置漏电保护器和电源开关。

#### Temporary electricity facilities should be installed in line with the requirements of the code leakage protector, mobile tools, handheld electric tools should be equipped with leakage protector and power switch one by one.

      - 临时用电单位未经批准，严禁向其他单位转供电或增加用电负荷，以及变更用电地点和用途。

#### Without approval, the temporary power consumption unit is strictly prohibited to transfer power supply to other units or increase the power load, and change the place and purpose of power consumption.

      - 用电结束后，用电单位应及时通知供电单位拆除临时用电线路。

#### After the end of power consumption, the power consumption unit shall promptly notify the power supply unit to remove the temporary power lines.

### 6.3.6动土作业 Excavation operation

6.3.6.1 作业单位（数据中心、客户、承包商、供应商等相关方）在开挖动土作业前需申请《开挖动土作业许可证》。《开挖动土作业许可证》有效期7天。

The operation unit (data center, customer, contractor, supplier and other relevant parties) shall apply for the Excavation and Earthmoving Operation Permit before the excavation and Earthmoving operation. The "Excavation moving Operation Permit" is valid for 7 days.

6.3.6.2动土作业前，应检查工具、现场支撑是否牢固、完好，发现问题应及时处理。

Before the earth-moving operation, check whether the tools and on-site supports are firm and intact, and deal with any problems in time.

6.3.6.3动土作业现场应根据需要设置护栏、盖板和警告标志，夜间应悬挂警示灯。在破土开挖前，应先做好地面和地下排水，防止地面水渗入作业层面造成塌方。

Guardrail, cover plate and warning signs should be set up at the site of earth moving operation according to needs, and warning lights should be hung at night. Before the ground excavation, the ground and underground drainage should be done first to prevent the ground water from penetrating into the working level and causing landslides.

6.3.6.4动土作业前应首先了解地下隐蔽设施的分布情况，动土临近地下隐蔽设施时，应使用适当工具挖掘，避免损坏地下隐蔽设施。如暴露出电缆、管线以及不能辨认的物品时，应立即停止作业，妥善加以保护，报告动土审批单位处理，经采取措施后方可继续动土作业。

Before moving soil operation, the distribution of underground concealed facilities should be understood first. When moving soil is near underground concealed facilities, appropriate tools should be used to dig to avoid damage to underground concealed facilities. If cables, pipelines and unidentifiable items are exposed, the operation should be stopped immediately, properly protected, reported to the ground moving examination and approval unit for handling, and the ground moving operation can be continued after taking measures.

6.3.6.5动土作业应设专人监护。挖掘坑、槽、井、沟等作业，应遵守下列规定：

Special personnel shall be assigned to supervise the earth moving operations. In digging pits, troughs, Wells, ditches and other operations, the following provisions shall be observed:

- 挖掘土方应自上而下逐层挖掘，不应采用挖底脚的办法挖掘。

Excavating earth should be excavated layer by layer from top to bottom, and should not be excavated by digging the bottom foot.

- 挖出的泥土应堆放在距坑、槽、井、沟边沿至少1m处，堆土高度不得大于1.5m。挖出的泥土不应堵塞下水道和窨井。

The excavated soil should be piled at least 1m away from the edge of the pit, trough, well and ditch, and the height of the mound should not be greater than 1.5m. The excavated soil should not block sewers and manholes.

- 不应在土壁上挖洞攀登。

No holes should be dug into the earth walls for climbing.

- 不应在坑、槽、井、沟上端边沿站立、行走。

Do not stand or walk on the edge of the top end of a pit, trough, well or ditch.

- 应视土壤性质、湿度和挖掘深度设置安全边坡或固壁支撑。作业过程中应对坑、槽、井、沟边坡或固壁支撑架随时检查，特别是雨雪后和解冻时期，如发现边坡有裂缝、松疏或支撑有折断、走位等异常情况，应立即停止工作，并采取相应措施。

Safety slope or solid wall support should be set depending on soil properties, humidity and digging depth. Pit, trough, well, ditch slope or solid wall support frame should be checked at any time during the operation, especially after rain and snow and thawing period, if the slope is found to have cracks, loose or support broken, go and other abnormal conditions, should immediately stop working, and take corresponding measures.

- 在坑、槽、井、沟的边缘安放机械、铺设轨道及通行车辆时，应保持适当距离，采取有效的固壁措施，确保安全。

When placing machinery, laying track and passing vehicles on the edge of the pit, trough, well and ditch, appropriate distance should be maintained and effective wall fixing measures should be taken to ensure safety.

- 在拆除固壁支撑时，应从下而上进行；更换支撑时，应先装新的，后拆旧的。

When removing the solid wall support, it should be carried out from the bottom up; When replacing the support, the new one should be installed first and the old one removed later.

- 不应在坑、槽、井、沟内休息。

It is forbidden to rest in pits, troughs, Wells or ditches.

6.3.6.6动土作业人员在沟（槽、坑）下作业应按规定坡度顺序进行，使用机械挖掘时不应进入机械旋转半径内；深度大于2m时应设置人员上下的梯子等，保证人员快速进出设施；2人以上作业人员同时挖土时应相距2m以上，防止工具伤人。

Earth-moving operators should work under the ditch (trough, pit) in accordance with the prescribed slope sequence, and should not enter the rotation radius of the machine when using mechanical excavation; When the depth is greater than 2m, ladders should be set up and down to ensure that personnel can quickly enter and exit the facility; When more than 2 workers dig at the same time, they should be more than 2m apart to prevent tools from hurting people.

6.3.6.7动土作业人员发现异常时，应立即撤离作业现场。

Earth-moving operators should immediately evacuate the work site when they find anomalies.

6.3.6.8动土作业结束后应及时回填土石，并恢复地面设施。

After the completion of the earth-moving operation, the earth and rock should be backfilled in time, and the ground facilities should be restored.

  - 作业变更 Change management

6.4.1 高风险作业内容变更、作业范围扩大、作业地点转移或超过作业许可有效期限时，应重新办理高风险作业许可证。

When the content of high-risk operations is changed, the scope of operations is expanded, the location of operations is transferred, or the period of validity of the work permit is exceeded, the high-risk operation permit shall be re-applied for.

6.4.2工艺条件、作业条件、作业方式或作业环境改变时，应重新进行作业危害分析，核对风险管控措施，应重新办理高风险作业许可审批。

When the technological conditions, working conditions, working methods or working environment change, the operation hazard analysis should be re-conducted, the risk control measures should be checked, and the high-risk operation license should be re-approved.

7附件 Attachments

- IF-PJ-EHS-1101《动火作业许可证》 Hot Work Permit

- IF-PJ-EHS-1102《高处作业许可证》Work-at-Height Permit

- IF-PJ-EHS-1103《吊装作业许可证》Lifting Operation Permit

- IF-PJ-EHS-1104《有限空间作业许可证》Confined Space Operation Permit

- IF-PJ-EHS-1105《临时用电作业许可证》Temporary Electricity Operation License

- IF-PJ-EHS-1106《开挖动土作业许可证》Excavation and Moving Earth Operation Permit

- IF-PJ-EHS-1107 上海浦江数据中心有限空间台账 SHANGHAI PUJIANG Data Center Confined Space Log