挂牌上锁（LOTO）管理制度

LOTO Management System

内部使用

在使用前，请和文档编写人员确认本文档为最新版本。

未经上海暻熠数据科技有限公司、上海暻耀网络技术有限公司书面许可，其它任何机构或个人不可传阅、引用或复制本文件的内容。

For Internal Use Only

Before using, check with the documentation writer to make sure this document is the latest version.

Without the written permission of Shanghai Jingyi Data Technology Co., Ltd., Shanghai Jingyao internet Technology Co., Ltd., no other organization or individual is allowed to circulate, quote or copy the content of this document.

| 文件编号Documents | IP-PJ-EHS-12 |
| --- | --- |
| 版 本Edition | V1.0 |
| 文件维护部门File maintenance department | 上海浦江数据中心 |
| 会签部门Document Signing department | 上海浦江数据中心 |
| 执行范围Scope of execution | 上海浦江数据中心 |

文件修订记录

Document revision record

| 版本号 Edition | 版本日期 Date | 修订内容 Revised Content | 修订人员 Revision personnel | 核准员 Approver | 备注 Remarks |
| --- | --- | --- | --- | --- | --- |
| V1.0 | 2025-04-16 | 首次修订 | 楚靖岳 | 陆磊 |  |

目录Content

1 目的Purpose	4

2 适用范围Scope of application	4

3 规范性应用文件Reference documents	4

4 术语和定义Terms and definitions	5

5 职责Responsibility	8

5.1 人力资源管理部门HR Department	8

5.2 EHS管理负责人EHS officer	8

5.3 各部门/岗位/业务线Each department/position/business line	9

6 程序Procedures	10

6.1 挂牌上锁LOTO程序LOTO program	10

6.2 挂牌上锁LOTO步骤及方法LOTO steps and methods 	13

6.3 LOTO培训计划LOTO training plan	18

6.4 LOTO培训要求LOTO training requirement	19

7 附件Attachments	21

- 目的Purpose

本制度目的是在于建立一套建立上海暻熠数据科技有限公司、上海暻耀网络技术有限公司（以下简称“上海浦江数据中心”）员工进行安全工作方法控制系统，防止机器的能量意外释放或传输，减少伤害员工和相关方人员的风险。本制度确定了预防危险性能源突发性释放造成伤害，保护人身安全的程序、技术、设计和方法的要求及实施目标。本制度规定了控制危险性能源的最低行为要求。

The purpose of this system is to establish a safety work method control system for employees of Shanghai Jingyi Data Technology Co., Ltd., Shanghai Jingyao internet Technology Co., Ltd. (Below referred to as "SHANGHAI Pujiang Data Center"), to prevent accidental release or transmission of machine energy and reduce the risk of injury to employees and related parties. This system establishes the requirements and implementation goals for procedures, technologies, designs, and methods to prevent the sudden release of hazardous energy and protect personal safety. This system stipulates the minimum behavioral requirements for controlling hazardous energy.

- 适用范围Scope of application

本制度适用不仅局限于在机器上、设施上或对电路进行的作业，在进行服务、维护时，主要能源、次要的储存/剩余能量源均需锁定。主要能量源是指为机器、设施和电路提供主要能量的能量源，如电能、气动能、液压能、机械能、化学能等。

This system is not limited to operations on machines, facilities, or circuits. During service and maintenance, both primary energy sources and secondary storage/surplus energy sources must be locked. The main energy source refers to the energy source that provides the main energy for machines, facilities, and circuits, such as electrical energy, pneumatic energy, hydraulic energy, mechanical energy, chemical energy, etc.

- 规范性应用文件Scope of application

GB/T 33579 机械安全 危险能量控制方法 上锁/挂牌

GB/T 33579 Mechanical Safety - Methods for Controlling Hazardous Energy - Lockout/Tagout

GB5083 生产设备安全卫生设计总则

GB5083 General Principles for Safety and Health Design of Production Equipment

GB 5226.1 机械安全 机械电气设备 第1部分：通用技术条件

GB 5226.1 Mechanical Safety - Electrical Equipment of Machinery - Part 1: General Technical Conditions

GB/T 19670 机械安全 防止意外启动

GB/T 19670 Mechanical safety - Prevention of accidental start-up

GB/T 24612.2 电气设备应用场所的安全要求第2部分：在断电状态下操作的安全措施

GB/T 24612.2 Safety Requirements for Electrical Equipment Application Sites Part 2: Safety Measures for Operation in Power Off State

GB 2894 安全标志及其使用导则

GB 2894 Safety Signs and Guidelines for their Use

- 术语和定义Terms and definitions

  - 授权人员Authorizing person

指经适当培训并被授权进行危险性能源控制（能量锁定LOTO）的人员。

Personnel who have received appropriate training and are authorized to carry out hazardous energy control (energy locking LOTO).

  - 受影响的人员Affected personnel

指按照能量锁定LOTO方案维护或保养设备的操作人员，或在进行此种维护或保养的区域工作的人员。（这些人员可能无权进行能量锁定LOTO）。

Refers to the operators who maintain or upkeep equipment according to the energy locked LOTO scheme, or the personnel working in the area where such maintenance or upkeep is carried out. (These personnel may not have the authority to perform energy locking LOTO).

  - 警报Alarm

对即将发生的危险，例如移位或某一机器、设施、工艺流程和线路发生停机或故障，向员工发出危险警报的视听装置。

A visual and auditory device that alerts employees of imminent danger, such as displacement or shutdown or malfunction of a machine, facility, process, or circuit.

  - 邻近或关联设备/工艺流程Adjacent or associated equipment/process flow

虽与机器、设施、工艺流程和线路的主要部分相连接，但其电源不依赖于该机器、设施、工艺流程和线路的能量源。

Although connected to the main parts of machines, facilities, processes, and circuits, its power supply does not depend on the energy source of the machines, facilities, processes, and circuits.

  - 控制回路Control loop

用以启动或中断机器能源的回路，也可以是用来控制机器性能但不直接中断能源的控制装置或系统的回路。控制回路可能采用液压、气动、机械传动等方式。

A circuit used to start or interrupt machine energy, or a control device or system circuit used to control machine performance without directly interrupting energy. The control circuit may adopt hydraulic, pneumatic, mechanical transmission and other methods.

  - 控制可靠性Control reliability

当设备或系统中的单个元件发生故障时，系统防止或阻止危险运动的能力。

The ability of a system to prevent or stop dangerous movements when a single component in a device or system fails.

  - 控制系统Control system

指机器、设施、工艺流程和线路的操作仪表或装置所配备的传感器、手动输入和模式选择装置、联锁和逻辑回路，以及输出装置。

Sensors, manual input and mode selection devices, interlocks and logic circuits, as well as output devices equipped with operating instruments or devices for machines, facilities, process flows, and circuits.

  - 得能Obtain energy

与能量供应装置相连或含有剩余或储存能量。

Connected to an energy supply device or containing surplus or stored energy.

  - 失能Losing energy

断开所有能源，并且不含剩余或储存能量。

Disconnect all energy sources and do not contain any remaining or stored energy.

  - 危险性能源Hazardous energy

任何可能造成人身伤害的能量，包括电气、机械、液压、气动、化学、热能、势能等。

Any energy that may cause personal injury, including electrical, mechanical, hydraulic, pneumatic, chemical, thermal, potential energy, etc.

  - 能源隔离装置Energy isolation device

物理防止能量传输或释放的机械装置，包括但不限于以下装置：手动电闸、断路开关、手动开关（可将电导体与所有未接地电源导体断开，并且任何一极均不能独立开启）、电线开关、阻塞装置和用于阻塞或绝缘能量的类似装置。

Mechanical devices that physically prevent energy transmission or release, including but not limited to the following: manual switches, circuit breakers, manual switches (which can disconnect electrical conductors from all ungrounded power conductors and neither pole can be independently opened), wire switches, blocking devices, and similar devices used for blocking or insulating energy.

  - 能量释放Energy release

将储存能量从机器、设施、工艺流程或线路中去除的作法。

The practice of removing stored energy from machines, facilities, processes, or circuits.

  - 上锁装置Locking device

一种可靠的主动装置，例如锁具，确保能量能源隔离装置处于安全状态，防止机器、设施、工艺流程和线路得能。

A reliable active device, such as a lock, ensures that the energy isolation device is in a safe state, preventing machines, facilities, processes, and circuits from being damaged.

  - 挂牌装置Hanging device

可视化的警告装置，以标记、标签、图案、布告或其他标识形式告知遵守者可能导致伤亡的潜在危险的性质和程度。可牢固固定在能量隔离装置上的突出警告装置，如标牌，以表明在移除挂牌装置以前不能操作被控制机构。

A visual warning device that informs followers of the nature and extent of potential hazards that may result in injury or death through markings, labels, patterns, notices, or other forms of identification. A protruding warning device, such as a sign, that can be securely fixed to the energy isolation device to indicate that the controlled mechanism cannot be operated until the hanging device is removed.

  - 能量锁定Energy locking

按照既定规程在能源隔离装置上安置锁具和标牌，以表明在锁具/标牌按照既定程序移除之前，不得操作能量隔离装置。

Install locks and tags on the energy isolation device according to established procedures to indicate that the energy isolation device cannot be operated until the locks/tags are removed according to established procedures.

  - 风险评估Risk assessment

对危险状态下的人身伤害或损害的可能性和程度的综合评估。风险评估用于选择适当的安全防护措施。

A comprehensive assessment of the likelihood and degree of personal injury or damage in a dangerous state. Risk assessment is used to select appropriate security measures.

  - 带能源作业的替代方法Alternative methods for energy operations

用于指导员工在不能够完整能量锁定LOTO时使用的最安全的程序。带能源作业的替代方法需基于对机器设备、工艺流程和线路的风险评估而制定。

Used to guide employees on the safest procedures to use when LOTO cannot be fully energy locked. Alternative methods for energy operations need to be developed based on risk assessments of machinery, equipment, process flow, and wiring.

- 职责Responsibilities

  - 人力资源管理部门

Human Resources Management Department

    - 统筹、计划本数据中心的挂牌上锁LOTO授权人员、受影响的人员分别进行相关知识、技能培训。

Coordinate and plan for LOTO authorized personnel and affected personnel in this data center to receive relevant knowledge and skills training.

    - 强化执行数据中心级挂牌上锁LOTO对应的奖惩制度，对违规者执行数据中心的纪律处罚规定。

Strengthen the implementation of the reward and punishment system corresponding to LOTO for data center level tagging and locking, and enforce the disciplinary punishment regulations of the data center for violators.

  - EHS管理负责人EHS officer

    - 制定保护生产操作人员免受危险性能量伤害的设备LOTO专属程序和相关任务清单。

Develop equipment LOTO exclusive procedures and related task lists to protect production operators from hazardous energy injuries.

    - 辨识、评估带能源操作LOTO替代方法工作的风险，确定适用的安全管理程序。

Identify and evaluate the risks associated with LOTO alternative methods of operating with energy, and determine the applicable safety management procedures.

    - 发放、定期维护LOTO授权人员使用的LOTO锁具、挂牌。

Distribute and regularly maintain LOTO locks and tags used by LOTO authorized personnel.

    - 确定本数据中心的LOTO授权人员名单。

Determine the list of LOTO authorized personnel for this data center.

    - 当设备发生变动、改造时，立即对上锁挂牌LOTO专属程序进行评估、更新。保持各个设备的具体的上锁挂牌程序文件适用性。

When the equipment undergoes changes or modifications, immediately evaluate and update the LOTO exclusive program for locking and tagging. Maintain the applicability of specific lockout and tagout procedure files for each device.

    - 开展和提供LOTO受影响人员意识培训和年度复训。

Conduct and provide LOTO affected personnel awareness training and annual refresher training.

    - 开展LOTO授权人员资格验证审核和日常检查。

Conduct LOTO authorized personnel qualification verification and daily inspections.

  - 各部门/岗位/业务线Departments/Positions/Business Lines

    - 对挂牌上锁LOTO项目推进进行协调。

Coordinate the progress of the LOTO project for tagging and locking.

    - 组织或参与对本数据中心的LOTO授权人员进行专业技能培训、考核。

Organize or participate in professional skills training and assessment for LOTO authorized personnel in this data center.

    - 组织或参与本数据中心的LOTO受影响的人员进行意识培训。

Organize or participate in awareness training for personnel affected by LOTO in this data center.

    - 协助本数据中心的EHS部门制定设备上锁挂牌LOTO专属程序。

Assist the EHS department of this data center in developing equipment lockout and tagout LOTO exclusive procedures.

    - 组织并协助定期的挂牌上锁LOTO专题检查，定期检查人员培训记录。

Organize and assist in regular LOTO special inspections for tagging and locking, and regularly check personnel training records.

    - 开展年度的挂牌上锁LOTO项目的评估，并对发现的问题提出更新改进建议。

Conduct an annual evaluation of the LOTO project for tagging and locking, and provide updated and improved suggestions for any identified issues.

- 程序Procedure

  - 挂牌上锁LOTO程序Tag out and Lock LOTO Procedure

    - 整个危险能源制度的一个重要元素是为所有机器、设施和电路配置制定《设备挂牌上锁LOTO专属程序》（详见附件1）。该程序需识别机器、设施、电路、组件的名称、能源类型、位置及将能量源降为零的方法。该程序应详细、具体至其所锁定的设备和隔离点位置信息。

    - 当各部门拥有一台以上类似的设备或一个以上相同的系统或工艺流程，且这些设备实际的能源隔离程序和能源隔离装置的位置一样，可对这些设备运用相同的设备挂牌上锁LOTO专属程序。

An important element of the entire hazardous energy system is the development of the "Equipment Tagging and Lockout LOTO Exclusive Procedure" for all machinery, facilities, and circuit configurations (see Annex 1 for details). This program needs to identify the names, energy types, locations, and methods of reducing energy sources to zero for machines, facilities, circuits, and components. The program should be detailed and specific to the location information of the locked devices and isolation points.

    - 当机器设备只有一种能源供应并且很容易识别和隔离，则不需要书面的设备挂牌上锁LOTO挂牌上锁LOTO专属程序。

When the machine equipment has only one energy supply and is easily identified and isolated, there is no need for a written equipment tagging and locking LOTO tagging and locking LOTO exclusive program.

    - 设备挂牌上锁LOTO专属程序的要素。程序应明确且特别地规定有效隔离机器、设施和电路的要求。应包括如下内容：

Elements of LOTO exclusive program for equipment tagging and locking. The program should clearly and specifically specify the requirements for effectively isolating machines, facilities, and circuits. It should include the following content:

  - 确定机器、设施和电路。

Identify machines, facilities, and circuits.

  - 能量源种类和量纲（如电压--380V，压缩空气--0.6MPa）.

Types and dimensions of energy sources (such as voltage -380V, compressed air -0.6MPa).

  - 所有需要的能源隔离装置信息。

All necessary information on energy isolation devices

  - 实现零能源状态的具体步骤 (关闭、隔离或围蔽机器、设施和电路以控制危险性能源。释放储存电能、势能或潜在能源）。

The specific steps to achieve a zero energy state (shutting down, isolating, or enclosing machines, facilities, and circuits to control hazardous energy. Releasing stored electrical energy, potential energy, or latent energy)

  - 测试机器、设施和电路以确定和验证危险性能源控制措施有效的具体步骤。

The specific steps to achieve a zero energy state (shutting down, isolating, or enclosing machines, facilities, and circuits to control hazardous energy. Releasing stored electrical energy, potential energy, or latent energy).

  - 放置或拆除上锁装置或挂牌装置的具体步骤。

The specific steps for placing or removing locking or hanging devices.

    - 数据中心应建立设备挂牌上锁LOTO专属程序书面的审核流程，以确保新机器、现有机器的改变或已识别的危险性能源控制缺陷的校正及控制改进等得到管控:

According to the center, a written review process for LOTO exclusive procedures for equipment tagging and locking should be established to ensure that new machines, changes to existing machines, or correction and control improvement of identified hazardous energy control defects are controlled:

  - 确认：负责设备挂牌上锁LOTO专属程序的授权人员应确认程序的准确性、完整性及能源控制的有效性。此类确认必须包含确定在执行挂牌上锁LOTO步骤时设备可以达到零能源状态。

Confirmation: The authorized personnel responsible for the LOTO exclusive program for equipment tagging and locking should confirm the accuracy, completeness, and effectiveness of the program for energy control. This type of confirmation must include confirming that the equipment can reach a zero energy state during the execution of the tagging and locking LOTO steps.

  - 批准：每一个设备挂牌上锁LOTO专属程序在实施前均需取得数据中心负责人或指定人员的批准。

Approval: The LOTO exclusive program for tagging and locking each device requires approval from the data center manager or designated personnel before implementation.

  - 文件维护：数据中心应通过文件管理系统确保程序及时更新。数据中心应定期审核程序以确保其符合现状。如某程序需修改，现有版本与以前的版本均应保留。应记载每个程序的变更日期、版本和更新。

File maintenance: The data center should ensure timely program updates through a file management system. Data centers should regularly review procedures to ensure compliance with current conditions. If a program needs to be modified, both the existing version and the previous version should be retained. The change date, version, and update of each program should be recorded.

    - 上锁装置和挂牌装置（参见附件2）。

Locking and hanging devices (see Attachment 2)

    - 实施能源隔离所适用的所有上锁装置和挂牌装置均应由数据中心提。

All locking and tagging devices applicable to the implementation of energy isolation shall be provided by the data center.

      - 每一个上锁装置和挂牌装置均应特别标明。

Each locking device and hanging device should be specifically labeled.

      - 只能用于控制危险性能源的唯一装置，不得用于其他目的。

The only device that can only be used to control hazardous energy and shall not be used for other purposes.

      - 上锁装置和挂牌装置应满足以下要求

Locking and hanging devices shall meet the following requirements：

  - 上锁和挂牌装置(包括其连接方式）应能够暴露的环境中经受预计暴露的最长期限。

The locking and tagging device (including its connection method) should be able to withstand the maximum expected exposure period in the exposed environment.

  - 对同一数据中心内，上锁和挂牌装置至少应在一方面标准化：颜色、形状、大小、或特定记号；对挂牌装置而言，图案和格式应标准化。

Locking and tagging devices within the same data center should be standardized in at least one aspect: color, shape, size, or specific markings; For hanging devices, patterns and formats should be standardized.

  - 上锁和挂牌装置，包括其固定装置，在未使强力或采取破坏性方式时，不应因无意的或偶然的动作而掉落。

Locking and tagging devices, including their fixing devices, should not fall off due to unintentional or accidental actions without the use of force or destructive methods.

  - 上锁和挂牌装置上应注明使用该装置的授权人员的信息。

The information of authorized personnel using the locking and tagging device should be indicated on the device.

  - 授权人员执行挂牌上锁LOTO时应附上红色标牌。红色标牌应包括“危险”信号词及使用挂牌上锁LOTO的日期。红色标牌将显示设备已被锁定，且服务、维护正在进行。标签上附注区可提供有关锁定、服务、维护条件的其他信息。

Authorized personnel should attach a red tag when performing tag up and lock LOTO. The red sign should include the word "danger" signal and the date of using the tag to lock LOTO. The red sign will indicate that the device has been locked and service and maintenance are in progress. The annotation area on the label can provide additional information about locking, service, and maintenance conditions.

  - 黄色标牌贴在机器、设施或电路上显示“运行中止”或不运转情形。黄色标牌不是挂牌上锁LOTO装置，它表明机器、设施或电路未在运转，亦未在进行任何服务、维护活动，应注明“小心”和“勿操作”。标签上备注区可提供有关锁定、服务、维护条件的其他信息。

Yellow signs are affixed to machines, facilities, or circuits to indicate 'suspended operation' or non operational status. The yellow sign is not a tag to lock the LOTO device, it indicates that the machine, facility, or circuit is not in operation, nor is any service or maintenance activity being carried out, and should indicate "Caution" and "Do Not Operate". The remarks section on the label can provide additional information about locking, service, and maintenance conditions.

  - 挂牌装置应采用牢固的和足够强度的方式，以免天气状况、干燥及湿润的位置或腐蚀性环境影响标签的内容使其无法辨认。

The hanging device should be sturdy and of sufficient strength to prevent weather conditions, dry and humid locations, or corrosive environments from affecting the content of the label and making it unrecognizable.

  - 挂牌装置应对接通机器或使设备得能的危险操作予以警告，包括诸如“请勿启动”或“请勿操作”的图标。

The hanging device should warn of dangerous operations that may involve connecting the machine or enabling the equipment, including icons such as "Do Not Start" or "Do Not Operate".

    - 所有的能源隔离装置应通过现场目视化准确标识，标识应能够经受预期的环境状况要求。设备挂牌上锁LOTO专属程序应通过照片、位置图或其他方式明确标明能源隔离装置的准确位置。便于识别能源隔离装置的目的减少导致授权人员发生隔离危险能源错误的原因。

All energy isolation devices should be accurately identified through on-site visualization, and the identification should be able to withstand the expected environmental conditions. The LOTO exclusive program for equipment tagging and locking should clearly indicate the accurate location of the energy isolation device through photos, location maps, or other means. The purpose of identifying energy isolation devices is to reduce the reasons for authorized personnel to make errors in isolating hazardous energy.

  - 挂牌上锁LOTO步骤及方法Steps and methods for tagging and locking LOTO

挂牌上锁LOTO只能由授权人员实施。授权人员包括但不限于维修工、工程师。授权人员使用数据中心所提供的个人LOTO锁和红色标牌隔离能量源。

Tagging and locking LOTO can only be carried out by authorized personnel. Authorized personnel include but are not limited to maintenance workers and engineers. Authorize personnel to use the personal LOTO lock and red label provided by the data center to isolate the energy source.

    - 准备停止关闭运行机器、设施和电路：授权人员应了解所适用的程序，取得所需要的保护材料和硬件，明确通知的要求，确定附近和关联的机器、设施和电路，并评估关闭能源的后果。通知有关人员：在实施之前及在拆除上锁装置或挂牌装置之后，均应通知可能受影响的人员（其中可能包括操作人员、工程师等）。

Prepare to stop the operation of machines, facilities, and circuits: Authorized personnel should understand the applicable procedures, obtain the necessary protective materials and hardware, clarify the notification requirements, identify nearby and associated machines, facilities, and circuits, and evaluate the consequences of shutting down energy. Notify relevant personnel: Prior to implementation and after removal of locking or tagging devices, personnel who may be affected (including operators, engineers, etc.) should be notified.

    - 停止关闭机器、设施和电路：授权人员应按照数据中心所确定的工作程序切断或关闭机器、设施、电路的能源。要求操作人员确保关闭的规范性以减少潜在的危险，降低对机器可能的损害。

Stop shutting down machines, facilities, and circuits: Authorized personnel should cut off or shut down the energy of machines, facilities, and circuits according to the work procedures determined by the data center. Require operators to ensure proper shutdown procedures to reduce potential hazards and minimize potential damage to the machine.

    - 隔离机器、设施和电路：授权人员应按照设备专有挂牌上锁LOTO程序亲自确定所有能源隔离装置(切断器、阀等）的位置。随后将此类装置定位（关闭、堵塞等）以阻止能源流入机器、设施和电路。授权人员应检查能源隔离装置的状况以及阻止能源流动的状况。

Isolation of Machines, Facilities, and Circuits: Authorized personnel shall personally determine the location of all energy isolation devices (cut-off devices, valves, etc.) in accordance with the LOTO procedure for equipment proprietary tagging and locking. Subsequently, such devices are positioned (closed, blocked, etc.) to prevent energy from flowing into machines, facilities, and circuits. Authorized personnel should inspect the condition of energy isolation devices and the prevention of energy flow.

    - 当隔离能源的同时还需要维持控制系统的运转或者是需要维持设施其他装置和部件的运作时，可对复杂的机器、设施和电路进行局部的挂牌上锁LOTO，此类状况可在设备挂牌上锁LOTO专属程序中予以规定，并通过风险评估认可。

When it is necessary to maintain the operation of the control system or other devices and components of the facility while isolating energy, complex machines, facilities, and circuits can be locally tagged and locked LOTO. Such situations can be specified in the equipment tagging and locking LOTO exclusive procedure and approved through risk assessment.

    - 使用锁定或挂牌装置：授权人员应使用上锁/挂牌装置并确保其正确使用。个人LOTO锁及红色标牌应固定在机器、设施、电路的能源隔离装置上（切断器、阀等）。当能源隔离装置无法直接放置锁具，应使用专用特殊锁具配合球阀、断路器的状况进行锁定，应注意必须遵循“一个工作人员，一把锁，一把钥匙”的原则。复杂的需要多人的操作中也可使用小组锁定。 锁定后核实能源隔离装置保持处于“安全”和“关闭”状态。当挂牌装置不能直接固定在能源隔离装置上，则应将其放置在距离能源隔离装置最近的地方或便于提醒人员注意的地方，以使任何可能会操作机器、设施或电路的人员立即发现。例如一台设备的电源隔离开关位于顶部，则应在操作盘上明显放置警告标签提醒人们不得使用该设备。

Use of locking or tagging devices: Authorized personnel should use locking/tagging devices and ensure their correct use. The personal LOTO lock and red label should be fixed on the energy isolation devices (disconnectors, valves, etc.) of machines, facilities, and circuits. When the energy isolation device cannot be directly locked, a special lock should be used in conjunction with the ball valve and circuit breaker to lock it. It should be noted that the principle of "one worker, one lock, one key" must be followed. Group locking can also be used in complex operations that require multiple people. After locking, verify that the energy isolation device remains in a "safe" and "closed" state. When the hanging device cannot be directly fixed on the energy isolation device, it should be placed in the nearest place to the energy isolation device or in a place that is convenient for reminding personnel to pay attention, so that any personnel who may operate the machine, facility or circuit can immediately notice it. For example, if the power isolation switch of a device is located at the top, a warning label should be prominently placed on the control panel to remind people not to use the device.

    - 释放控制储存能源：授权人员应确保所有潜在危险性能源（储存的、剩余的、化学的或潜在的）均已被释放、流出或通过其他方式得以控制。还可采取其他措施防止能源的重新聚集。储存能源包括蓄电池、电容、重力、补偿水池、化学管道和弹簧。

Release control of stored energy: Authorized personnel shall ensure that all potentially hazardous energy (stored, surplus, chemical, or potential) has been released, leaked, or otherwise controlled. Other measures can also be taken to prevent the re aggregation of energy. Energy storage includes batteries, capacitors, gravity, compensating water tanks, chemical pipelines, and springs.

    - 核实隔离零能源状态：授权人员应在对已经锁定的机器、设施、电路核实是否已经按照设备专有挂牌上锁LOTO程序完成隔离和切断能源。核实结果必须确认机器、设施和电路已经处于零能源状态，如电力为零，气压为零，液体或气体压力为零等（测定零能源状态可通过测试设备、尝试激活电路、精密仪器或通过目测观察等完成）。

Verification of Isolation Zero Energy Status: Authorized personnel should verify whether the locked machines, facilities, and circuits have been isolated and cut off from energy in accordance with the equipment specific tagging and locking LOTO procedure. The verification results must confirm that the machines, facilities, and circuits are in a zero energy state, such as zero electricity, zero air pressure, zero liquid or gas pressure, etc. (Determining the zero energy state can be done through testing equipment, attempting to activate circuits, precision instruments, or visual observation, etc.).

    - 恢复工作：授权人员在恢复设备运转之前应实施以下活动

Recovery Work: Authorized personnel should carry out the following activities before restoring equipment operation：

  - 检查工作区域确保次要物品已经被移走，防护罩已经到位，机器、设施或电路运转正常，所有人员均处于安全位置。

Check the work area to ensure that secondary items have been removed, protective covers are in place, machines, facilities, or circuits are functioning properly, and all personnel are in a safe position.

  - 由实施的授权人员或当授权人员缺位时，需确保当该LOTO装置的授权人员回到现场时，被通知到其锁、标签、上锁装置已从每一个能源隔离装置上移走。

When authorized personnel are present or absent, it is necessary to ensure that when the authorized personnel of the LOTO device return to the site, they are notified that their locks, tags, and locking devices have been removed from each energy isolation device.

  - 通知受影响人员机器、设施和电路的能源将恢复。

Notify affected personnel that the energy of machines, facilities, and circuits will be restored

  - 通过目测检查、循环测试服务、维护任务已经完成。如任务已经完成，则机器、设施、电路可恢复工作。如未完成，则重复必要的挂牌上锁LOTO步骤。

The visual inspection, cyclic testing service, and maintenance tasks have been completed. If the task has been completed, the machines, facilities, and circuits can resume operation. If not completed, repeat the necessary tagging and locking LOTO steps.

  - 遵守正确的设备或电路的后续启动步骤。

Follow the correct subsequent startup steps for equipment or circuits.

    - 其他特殊注意事项Other special precautions

  - 未经LOTO授权人员同意之前，受影响人员不得进行任何机器操作、调整工作。

Without the consent of authorized personnel from LOTO, affected personnel are not allowed to perform any machine operations or adjustments.

  - 当一台机器有不止一个LOTO授权人员进行作业，则每个LOTO授权人员都应附上各自的锁具和标签。

When a machine is operated by more than one LOTO authorized personnel, each LOTO authorized personnel should attach their own lock and label.

  - 当LOTO授权人员的作业尚未完成却又分配新的工作，而机器又不得不保持上锁，则其他相关的人员在LOTO授权人员移除其锁具/挂牌之前应通知设备主管进行挂牌上锁LOTO交接过渡给其他授权人员给机器挂牌上锁。

When the LOTO authorized personnel have not yet completed their work but are assigned new tasks, and the machine has to be kept locked, other relevant personnel should notify the equipment supervisor to tag and lock the machine before the LOTO authorized personnel remove their locks/tags. LOTO handover should be handed over to other authorized personnel to tag and lock the machine.

  - 能量隔离装置附上锁具或标签后，任何人都不得尝试进行更改隔离状态。

After attaching locks or labels to the energy isolation device, no one is allowed to attempt to change the isolation status.

  - 当对电气隔离开关上锁，应尝试操作所有控钮，以核实设备处于零能源状况。

When locking the electrical isolation switch, attempt to operate all control buttons to verify that the equipment is in a zero energy state.

  - 在一般情况下，不得随意移除正在使用中的LOTO锁具/标签。

In general, LOTO locks/labels that are in use should not be removed arbitrarily.

  - 用作挂牌上锁用的锁具和标签不应被用于其他任何目的。

Locks and labels used for hanging and locking should not be used for any other purpose.

  - 设备主管应当给长时间（超过一个班次）停止运行的机器上停用锁。

The equipment supervisor should put a stop lock on machines that have stopped running for a long time (more than one shift).

  - 应向外部承包商告知挂牌上锁程序，并要求其遵守。

External contractors should be informed of the tagging and locking procedures and required to comply with them.

    - 锁的类型和用途Types and uses of locks

本制度中三类不同锁的类型和用途详见表1。

The types and purposes of the three different types of locks in this system are detailed in Table 1.

表1 锁的用途 Table 1: Purpose of Locks

| 锁的类型 Type of lock | 目的 objective | 使用期限 service life | 锁的颜色 The color of the lock | 钥匙 Key | 标签 Label |
| --- | --- | --- | --- | --- | --- |
| 个人锁 Personal lock | 仅可分配给授权人员并仅由其个人使用 Can only be assigned to authorized personnel and for their personal use only | 仅可单班次使用 Only available for single shift use | 不要求特别颜色，但一般使用红色，必须是独特的且仅可用于挂牌上锁LOTO No special color is required, but red is generally used. It must be unique and can only be used for tagging and locking LOTO | 仅有一把钥匙，不得配置万能钥匙 Only one key is allowed, and a master key cannot be configured | 建议红色标牌 Suggest red signage |
| 交接班锁/设备停用锁 Shift handover lock/equipment shutdown lock | 在设备或工艺流程无法及时运转时使用 Used when equipment or process cannot operate in a timely manner | 允许多班次使用 Allow multiple shifts to be used | 不要求特别颜色，但一般使用黄色，锁必须是独特的且仅可用于挂牌上锁LOTO No special color is required, but yellow is generally used. The lock must be unique and can only be used for hanging and locking LOTO | 可配置多把钥匙，但仅可由小型的管理小组控制和取得钥匙 Multiple keys can be configured, but can only be controlled and accessed by a small management team | 建议黄色标牌 Suggest yellow signage |
| 通用锁 Universal lock | 使用复杂/小组挂牌上锁LOTO时，不得指派单个员工锁定单个能源隔离装置或能量源 When using complex/group tagging to lock LOTO, it is not allowed to assign a single employee to lock a single energy isolation device or energy source | 允许多班次使用 Allow multiple shifts to be used | 不要求特别颜色，但一般使用蓝色，但锁必须是独特的且仅可用于挂牌上锁LOTO No special color is required, but blue is generally used. However, the lock must be unique and can only be used for hanging and locking LOTO | 仅有一把钥匙，不得配置万能钥匙 Only one key is allowed, and a master key cannot be configured | 通用锁平常放在公共锁站中，使用时做好记录。 Universal locks are usually placed in public lock stations, and records should be kept when used. |

  - LOTO培训计划 LOTO training plan

    - 培训计划需求Training plan requirement

LOTO授权人员及受影响的人员都应接受挂牌上锁LOTO的意识培训，以了解该程序制定的意义和要求。LOTO授权人员在正式得到授权之前必须接受初始授权培训及考核，以保证其能够正确、安全地运用挂牌上锁步骤。参见表2培训要求概要和表3培训频率要求组织进行培训。

LOTO authorized personnel and affected individuals should receive awareness training on tagging and locking LOTO to understand the significance and requirements of this procedure. LOTO authorized personnel must undergo initial authorization training and assessment before officially obtaining authorization to ensure that they can correctly and safely apply the tagging and locking steps. Refer to Table 2 for a summary of training requirements and Table 3 for training frequency requirements for organizing training.

表2 培训要求概要 Table 2 Summary of Training Requirements

| / | 受影响的人员Affected personnel | 授权人员authorizing officer |
| --- | --- | --- |
| 适用范围scope of application | 是Yes | 是Yes |
| 术语定义Definitions | 是Yes | 是Yes |
| 挂牌上锁基本要Basic elements of tagging and locking | 是Yes | 是Yes |
| 职责要求Job requirements | 是Yes | 是Yes |
| 设备挂牌上锁LOTO的专属程序Exclusive procedure for equipment tagging and locking LOTO | 否No | 是Yes |
| 挂牌上锁的执行步骤Execution steps for tagging and locking | 否No | 是Yes |
| 轮班人员变化Shift personnel changes | 否No | 是Yes |
| 带能源作业的替代方法Alternative methods for energy operations | 否No | 是Yes |

* 必须理解当轮班变化时挂牌上锁LOTO的连续性。

It is necessary to understand the continuity of tagging and locking LOTO when shifts change.

表3 培训频率要求 Table 3 Training Frequency Requirements

| / | 受影响的人员Affected personnel | 授权人员authorizing officer |
| --- | --- | --- |
| 意识培训awareness training | 必需的 (按表3中所列主题） Necessary (According to the themes listed in Table 3) | 必需的 (按表3中所列主题） Necessary (According to the themes listed in Table 3) |
| 初始授权培训及考核Initial authorization training and assessment | 不适用Not Applicable | 必需的 (必须由另一名授权员工进行观测和核查，也就是“实际演示”） Necessary (Must be observed and verified by another authorized employee, i.e. 'actual demonstration') |
| 一年一次的复训 Annual refresher training | 推荐recommend | 推荐recommend |
| 一年一次的演示Annual demonstration | 不适用Not Applicable | 必需的 (必须由另一名授权员工进行观测和核查，也就是“实际演示”） Necessary (Must be observed and verified by another authorized employee, i.e. 'actual demonstration') |

  - LOTO培训要求 LOTO training requirements

    - 受影响的人员的培训Training for affected personnel

数据中心应向受影响的人员提供挂牌上锁LOTO意识培训。该培训使受影响的人员可以确认挂牌上锁LOTO的情况，理解他们的责任是杜绝发生可能影响损害挂牌上锁LOTO的行为。

The data center should provide LOTO awareness training on tagging and locking to affected personnel. This training enables affected personnel to confirm the situation of tagging and locking LOTO, and understand their responsibility to prevent any behavior that may affect the tagging and locking LOTO.

培训的要求和目标如下：

The requirements and objectives of the training are as follows:

      - 数据中心培训应具体针对现场实际状况开展。

Data center training should be tailored to the actual on-site conditions.

      - 受影响的人员应认识到授权员工正在为需要挂牌上锁LOTO的机器、设施、加工和工艺流程提供服务、维护。受影响的人员应能明白确定锁定的设备影响范围。

Affected personnel should be aware that authorized employees are providing services and maintenance for machines, facilities, processes, and workflows that require LOTO tagging and locking. The affected personnel should be able to clearly determine the scope of impact of the locked equipment.

      - 受影响的人员对轮班或人员更换挂牌上锁LOTO的变化应有一个基本理解。

The affected personnel should have a basic understanding of the changes in LOTO for shift work or personnel replacement, including tagging and locking.

      - 受影响的人员应认识到LOTO标牌意味着“禁止操作”的情况。

The affected personnel should be aware that the LOTO sign indicates a situation of "prohibited operation".

    - 授权人员的培训Training of authorized personnel

在授权人员实施挂牌上锁LOTO之前，数据中心应提供初始授权培训，该培训将证明所有授权人员都理解能量制度的目的和功能。

Before authorizing personnel to implement tag out and lock LOTO, the data center should provide initial authorization training that will demonstrate that all authorized personnel understand the purpose and function of the energy system.

培训要求及培训目标如下The training requirements and objectives are as follows：

      - 数据中心培训应具体针对现场实际状况开展。

Data center training should be tailored to the actual on-site conditions.

      - 应向现场维护人员提供有关安全用电和数据中心挂牌上锁LOTO制度的培训。

Training on safe electricity usage and LOTO system for data center tagging and locking should be provided to on-site maintenance personnel.

      - 应向每一位授权人员提供其可能在服务、维护中遇到的能源类型以及控制和隔离该能源的方法的培训。

Each authorized personnel should be provided with training on the types of energy they may encounter during service and maintenance, as well as methods for controlling and isolating that energy.

      - 对所有进行的挂牌上锁LOTO初始授权的和额外的培训，数据中心均应记录。记录文件中应包括每一位人员的姓名、培训日期及培训主题。

The data center shall record all initial authorization and additional training related to LOTO tagging and locking. The record file should include the name, training date, and training topic of each personnel.

      - 每一位完成培训的人员在获得授权之前，必须完成至少一个设备的挂牌上锁LOTO专属程序，并且必须向至少一位授权员工完整演示挂牌上锁LOTO的步骤实际演示。

Before obtaining authorization, each person who completes the training must complete at least one device's LOTO exclusive procedure for tagging and locking, and must demonstrate the actual steps of tagging and locking LOTO to at least one authorized employee.

      - 各部门应确保授权人员准确理解数据中心专有挂牌上锁LOTO制度。培训中所涉及的信息的记录应予以保存。

Each department should ensure that authorized personnel accurately understand the proprietary LOTO system for data center tagging and locking. The records of the information involved in the training should be kept.

      - 培训方法可包括但不限于正式的指导、提供课程培训、电脑培训或互动培训。

Training methods may include but are not limited to formal guidance, providing course training, computer training, or interactive training.

      - 应每年进行一次挂牌上锁LOTO实际演示以保证授权人员对挂牌上锁LOTO的掌握程度。

An annual practical demonstration of LOTO tagging and locking should be conducted to ensure that authorized personnel have a good understanding of LOTO tagging and locking.

    - 其他培训Other Training

      - 当授权人员的工作任务发生变化或机器、设施或电路的变化导致新的危险或能源制度发生变化，则应向授权人员提供再次培训。

When there are changes in the work tasks of authorized personnel or changes in machines, facilities, or circuits that result in new hazards or changes in energy systems, re training should be provided to authorized personnel.

      - 任何时候审核显示或各部门有其他理由相信授权人员对能源制度的知识或实际应用与要求不符或不一致，应立即提供额外培训。

At any time when the audit shows or each department has other reasons to believe that the authorized personnel's knowledge or practical application of the energy system does not meet or is inconsistent with the requirements, additional training should be provided immediately.

- 附件attachments

- IF-PJ-EHS-1201：设备挂牌上锁LOTO专属程序 模板LOTO exclusive program template for equipment tagging and locking

- IF-PJ-EHS-1202：能量锁定LOTO锁具清单List of Energy Locked LOTO Locks