劳动防护用品配备和使用管理制度

Personal Protective Equipment Management System

内部使用

在使用前，请和文档编写人员确认本文档为最新版本。

未经上海暻熠数据科技有限公司、上海暻耀网络技术有限公司书面许可，其它任何机构或个人不可传阅、引用或复制本文件的内容。

Internal use

Before using, check with the documentation writer to make sure this document is the latest version.

Without the written permission of Shanghai Jingyi Data Technology Co., Ltd., Shanghai Jingyao internet Technology Co., Ltd., no other organization or individual is allowed to circulate, quote or copy the content of this document.

| 文件编号Documents | IP-PJ-EHS-16 |
| --- | --- |
| 版 本Edition | V1.0 |
| 文件维护部门File maintenance department | 上海浦江数据中心 |
| 会签部门Document Signing department | 上海浦江数据中心 |
| 执行范围Scope of execution | 上海浦江数据中心 |

文件修订记录

Document revision record

| 版本号 Edition | 版本日期 Date | 修订内容 Revised Content | 修订人员 Revision personnel | 核准员 Approver | 备注 Remarks |
| --- | --- | --- | --- | --- | --- |
| V1.0 | 2025-04-16 | 首次修订 | 楚靖岳 | 陆磊 |  |

目录Content

1目的 Purpose	4

2适用范围 Scope of application	4

3 规范性引用文件 Reference documents	4

4术语和定义Terms and definitions	5

5 职责 Responsibilities	5

5.1各部门/岗位/业务线 Departments/positions/lines of business	5

5.2采购人员 Procurement Personnel	5

5.3 EHS管理负责人 EHS officer	6

6程序 Procedures	6

6.1劳动防护用品配备原则 Principles of personal protective equipment	6

6.2职业性危害因素辨识和评估 Identification and assessment of occupational hazard factors	7

6.3劳动防护用品的配备 Equipment of protective articles	10

6.4追踪溯源 Tracing	12

6.5判废和更换 Rejection and replacement	13

6.6 验证与监控 Verification and monitoring	14

6.7沟通与培训 Communication and training	15

7	附件 Attachments	16

1目的 Purpose

本制度旨在建立上海暻熠数据科技有限公司、上海暻耀网络技术有限公司（以下简称“上海浦江数据中心”）劳动防护用品配备和使用管理流程。目标包括确保遵守国家和地方法律法规、国外相关法规、客户要求以及上海浦江数据中心内部要求，确保劳动防护用品配备和使用管理合规，降低运营EHS风险，并促进持续改进。

The purpose of this system is to establish Shanghai Jingyi Data Technology Co., Ltd., Shanghai Jingyao internet Technology Co., Ltd.. (hereinafter referred to as "SHANGHAI Pujiang Data Center"). labor protection equipment and use management process. The objectives include ensuring compliance with national and local laws and regulations, relevant foreign regulations, customer requirements and internal requirements of SHANGHAI PUJIANG Data Center, ensuring compliance with labor protective equipment installation and use management, reducing operational EHS risks, and promoting continuous improvement.

2适用范围 Scope of application

适用于上海浦江数据中心，以及所有与EHS有关事项的管理职能部门/岗位/业务线。

Applicable to SHANGHAI PUJIANG data Center and all management functions/positions/business lines related to EHS.

3 规范性引用文件 Reference documents

《中华人民共和国安全生产法》（2021年修订）

Work Safety Law of the People's Republic of China (revised in 2021)

《中华人民共和国职业病防治法》（主席令第24号，2018年修订）

Law of the People's Republic of China on the Prevention and Control of Occupational Diseases (Order of the President No. 24, revised in 2018)

《工作场所职业卫生管理规定》（中华人民共和国国家卫生健康委员会令第5号）

Regulations on the Administration of Occupational Health in Workplaces (Decree No. 5 of the National Health Commission of the People's Republic of China)

《用人单位劳动防护用品管理规范》（安监总厅安健〔2018〕3号）

Regulations on the Administration of Labor Protective Articles for Employers (2018) No. 3 of the General Department of Work Safety Supervision)

《职业病危害因素分类目录》（国卫疾控发〔2015〕92号）

Classification of Occupational Disease Hazard Factors (National Health Disease Control and Prevention (2015) No. 92)

GB 39800.1   个体防护装备配备规范 第1部分：总则

Specification for the provision of personal protective equipment -- Part 1: General provisions

DB 13/T 5614  变配电室安全管理规范（河北省）

DB 13/T 5614  Substation Safety management code (Hebei Province)

4术语和定义Terms and definitions

4.1个体防护装备（劳动防护用品）Personal protective equipment

从业人员为防御物理、化学、生物等外界因素伤害所穿戴、配备和使用的护品的总称。

Practitioners for the defense of physical, chemical, biological and other external factors to wear, equipped and use the general term of protective products.

4.2职业性危害因素 Occupational hazard factors

识别危险源的存在并确定其特性的过程。在职业活动中产生的可直接危害劳动者身体健康和安全的因素。按其性质分为物理性危害因素、化学性危害因素和生物性危害因素。

The process of identifying the presence of a hazard and determining its characteristics. Factors arising in occupational activities that may directly endanger the health and safety of workers. According to its nature, it can be divided into physical hazard factors, chemical hazard factors and biological hazard factors.

5 职责 Responsibilities

## 5.1各部门/岗位/业务线 Departments/positions/lines of business

5.1.1正确使用和保管劳动防护用品。

Proper use and storage of labor protective articles.

5.1.2定期对所使用的劳动防护用品进行检查，发现损坏或检验有效期失效等情况及时上报至EHS管理负责人。

Check the used labor protective articles regularly, and report to the EHS officer in time if any damage or expiration of inspection period is found.

5.1.3发现所在部门/岗位/业务线人员发现现场运营活动、设备设施或者使用的化学品等有较大变更，及时告知EHS管理负责人，确定是否存在职业病危害因素变更以及劳动防护用品变更。

The department/post/business line personnel shall inform the EHS officer in time of any major changes in site operation activities, equipment and facilities, or chemicals used, and determine whether there are any changes in occupational-disease-inductive factors and labor protective articles.

## 5.2采购人员 Procurement Personnel

5.2.1负责确定能够提供符合标准以及数据中心需求的劳动防护用品供应商。

Responsible for identifying labor protection equipment suppliers that can meet the standards and requirements of the data center.

5.2.2负责采购符合标准要求的劳动防护用品。

Be responsible for purchasing labor protection supplies that meet the requirements of the standards.

## 5.3 EHS管理负责人 EHS officer

5.3.1负责组织制定劳动防护用品配备和使用管理制度。

Responsible for organizing the formulation of the management system for the equipment and use of labor protective equipment.

5.3.2负责劳动防护用品配备和使用管理全过程监督管理。

Responsible for the supervision and management of the whole process of the allocation and use of labor protective articles.

5.3.3组织各部门/岗位/业务线进行劳动防护用品配备和使用相关培训。

Organize various departments/posts/business lines to conduct training on the equipment and use of labor protective articles.

5.3.4制定数据中心劳动防护用品配备清单，并及时更新。

Develop the list of labor protective equipment for data center and update it timely.

6程序 Procedures

## 6.1劳动防护用品配备原则 Principles of personal protective equipment

6.1.1数据中心作业场所中存在职业性危害因素和危害风险时，数据中心应为作业人员配备符合国家标准或行业标准的劳动防护用品。

When there are occupational hazard factors and hazard risks in the workplace of the data center, the data center shall equip the workers with labor protection articles that meet the national standards or industry standards.

6.1.2数据中心为作业人员配备的劳动防护用品应与作业场所的环境状况、作业状况、存在的危害因素和危害程度相适应，应与作业人员相适合，且劳动防护用品本身不应导致其他额外的风险。

The labor protection articles for the workers in the data center shall be adapted to the environmental conditions, operating conditions, existing hazard factors and degree of harm of the workplace, and shall be suitable for the workers, and the labor protection articles themselves shall not lead to other additional risks.

6.1.3数据中心配备劳动防护用品时，应在保证有效防护的基础上，兼顾舒适性。

When the data center is equipped with labor protective articles, comfort should be taken into account on the basis of ensuring effective protection.

6.1.4需要同时配备多种劳动防护用品时，应考虑使用的兼容性和功能替代性，确保防护有效。

When it is necessary to be equipped with multiple labor protective articles at the same time, the compatibility and functional substitution of the use should be considered to ensure effective protection.

6.1.5数据中心应对其使用的劳务派遣工、临时聘用人员，接纳的实习生和允许进入作业地点的其他外来人员与相关方共同配合进行劳动防护用品的配备及管理。

The data center shall cooperate with relevant parties in the provision and management of labor protection equipment for its dispatched workers, temporary employees, interns and other foreign personnel allowed to enter the work site.

6.1.6数据中心可参照《个体防护装备配备规范 第1部分：总则》（GB 39800.1）要求进行劳动防护用品的配备及管理。

Data centers may refer to the Specification for the Provision of Personal Protective Equipment Part 1: General Provisions (GB 39800.1) for the provision and management of labor protective equipment.

## 6.2职业性危害因素辨识和评估 Identification and assessment of occupational hazard factors

6.2.1职业性危害因素的辨识 Identification of occupational hazard factors

6.2.1.1辨识原则 Identification principles

职业性危害因素的辨识原则如下The identification principles of occupational hazard factors are as follows:

- 应依据国家及地方法律、法规、标准及专业知识，针对数据中心不同作业场所、生产运营工艺、作业环境的特点，识别可能的职业性危害因素。

Possible occupational hazard factors should be identified according to national and local laws, regulations, standards and professional knowledge, and according to the characteristics of different workplaces, production and operation processes and working environments of data centers.

- 应对生产经营活动中各因素，包括人员、设备设施、使用物料、工艺方法、环境条件、管理制度等进行系统分析。不仅应分析正常生产操作中存在的职业性危害因素，还应分析技术、材料、工艺等发生变化、设备故障或失效、人员操作失误等情况下可能产生的职业性危害因素。

The factors in the production and operation activities, including personnel, equipment and facilities, materials used, process methods, environmental conditions, management system and so on, should be systematically analyzed. It should not only analyze the occupational hazard factors existing in normal production operations, but also analyze the occupational hazard factors that may occur under the circumstances of changes in technology, materials and processes, equipment failure or failure, and personnel operation errors.

6.2.1.2辨识方法 Occupational hazard assessment

6.2.1.2.1应采用现场调査、测量，查阅相关记录，询问与交流等方式对作业环境中的职业性危害因素进行分析。

The occupational hazard factors in the working environment shall be analyzed by means of field investigation, measurement, reference to relevant records, inquiry and communication.

6.2.1.2.2在识别职业性危害因素时，应主要从以下方面进行分析:

When identifying occupational hazard factors, analysis should be carried out mainly from the following aspects:

- 正常工作状态；

Normal working condition.

- 异常工作状态；

Abnormal working condition.

- 人员作业活动；

Personnel operation activities.

- 设备采购、贮存和输送，以及设备设施的运行、维修和保养；

Equipment procurement, storage and transmission, and operation, repair and maintenance of equipment and facilities.

- 原辅材料、中间产品和最终产品（目前数据中心还未涉及，后续如涉及需要考虑到）；Raw and auxiliary materials, intermediate products and final products (currently not involved in the data center, and need to be taken into account if involved in the future).

- 生产、施工工艺；（通用术语，实际为数据中心运营特点）；

Production and construction technology; (general term, actual data center operation characteristics).

- 环境条件；

Environmental conditions.

- 管理制度；

Management system.

- 其他辅助活动和意外情况。

And other ancillary activities and contingencies.

6.2.2职业性危害评估 Occupational hazard assessment

应依据国家法规、标准等由专业人员对所识别的职业性危害因素进行评估，判断是否超过职业接触限值和实际的危害水平，结合危害因素存在的位置、危害方式、危害发生的时间、途径及后果，确定需要防护的人群范围，以及各类人员需要防护的部位和需要的防护水平。

6.2.3劳动防护用品配备流程如下[引用自《个体防护装备配备规范 第1部分：总则》（GB 39800.1）]。

Should be in accordance with the national regulations, standards and other professional assessment of the identified occupational hazard factors, determine whether the occupational exposure limit and the actual level of harm, combined with the location of the hazard factors, the way of harm, the time, way and consequences of the hazard, determine the need to protect the range of people, as well as all types of personnel need to protect the site and the required level of protection.

6.2.3 The procedure for the provision of labor protective equipment is as follows [quoted from the Specification for the Provision of Personal Protective Equipment Part 1: General Provisions (GB 39800.1)].

图1 劳动防护用品配备流程

## 6.3劳动防护用品的配备 Equipment of protective articles

6.3.1数据中心应建立健全劳动防护用品管理制度，至少应包括采购、验收、保管、选择、发放、使用、报废、培训等内容，并应建立健全劳动防护用品管理档案。

The data center shall establish and improve the management system of labor protective articles, which shall at least include procurement, acceptance, storage, selection, distribution, use, scrap, training and other contents, and shall establish and improve the management files of labor protective articles.

6.3.2数据中心EHS管理负责人应与采购合作，以识别和确定使劳动防护用品供应商有资格，确保所购买的劳动防护用品符合法规或认证机构标准（例如，中国GB、美国ANSI、欧盟CE等）。

The head of Data center EHS management shall work with the procurement to identify and determine the qualification of labor protection suppliers to ensure that the purchased labor protection products comply with regulations or certification body standards (e.g. GB in China, ANSI in the United States, CE in the European Union, etc.).

6.3.3应正确选择、安装和维护劳动防护用品。员工应在适当的时候参与选择劳动防护用品。

Labor protection products should be correctly selected, installed and maintained. Employees shall participate in the selection of labor protective equipment at appropriate times.

6.3.4数据中心应在入库前对劳动防护用品进行进货验收，确定产品是否符合国家或行业标准；对国家规定应进行定期强检的劳动防护用品（如绝缘垫等），用人单位应按相关规定，委托具有检测资质的检验检测机构进行定期检验。

The data center shall conduct incoming acceptance of labor protection supplies before warehousing to determine whether the products meet national or industry standards; For the labor protection articles (such as insulation MATS, etc.) that should be inspected regularly according to the state regulations, the employer shall entrust a qualified inspection and testing institution to conduct regular inspection according to the relevant provisions.

6.3.5在作业过程中发现存在其他危害因素，现有劳动防护用品不能满足作业安全要求，需要另外配备时，应立即停止相关作业，按照本部分的要求配备相应的劳动防护用品后，方可继续作业。

When other hazardous factors are found in the process of operation, the existing labor protective articles cannot meet the safety requirements of operation, and additional equipment is needed, the relevant operations shall be stopped immediately, and the corresponding labor protective articles shall be equipped in accordance with the requirements of this part before the operation can continue.

6.3.6适用时，应识别使用劳动防护用品所需的健康证明和医学监护要求（例如，呼吸器、听力保护装置等）并采取的措施。

a.仅为被认为身体符合的员工（当有要求时应通过医学评估）配备劳动防护用品。

If applicable, the health certificate and medical monitoring requirements (e.g., respirator, hearing protection device, etc.) required for the use of labor protective equipment should be identified and the measures taken.

a. Only employees who are deemed physically fit (and should pass a medical assessment when required) shall be equipped with labor protective equipment.

6.3.7使用后，PPE应整理干净并存放在指定区域。

After use, PPE should be cleaned and stored in a designated area.

6.3.8应为参观者提供适当的劳动防护用品，对识别出的他们拟访问区域的危害加以防护。

Visitors should be provided with appropriate Labor protection equipment to protect against identified hazards in the areas they intend to visit.

6.3.9在数据中心现场工作的承包商应为自己的员工提供劳动防护用品。

Contractors working on the site of the data center shall provide their own employees with labor protective equipment.

6.3.10数据中心劳动防护用品配备标准见表1。若数据中心有新、改、扩建项目或者技术改造项目等，经过职业病危害评价工作，确认有新增职业病危害因素，则需在现有基础上，重新辨识所需的劳动防护用品，并填报附件1。

The data center labor protection equipment standards are shown in Table 1. If the data center has a new, renovation, expansion project or technical transformation project, and the occupational-disease-inductive evaluation work confirms that there are new occupational-disease-inductive factors, it is necessary to re-identify the required labor protective articles on the existing basis and fill in Attachment 1.

表1 数据中心劳动防护用品配备标准

Table 1 Equipment standard of labor protective articles for data center

| 序号 No. | 作业活动 Activity | 示例 Example | 作业时包括下列防护用品，包括但不限于 PPE required |
| --- | --- | --- | --- |
| 1 | 登高作业 High altitude | 室外冷却塔清洗作业 Outdoor cooling tower cleaning | ①安全帽 Safety helmet ②反光背心 Reflective vest ③安全带 Safety belt ④安全鞋Safety shoes |
| 2 | 密闭空间作业 In confined spaces | 柴油罐储罐内部清洗 Diesel tank cleaning | ①安全帽 Safety helmet ②防毒面具Gas mask ③反光背心 Reflective vest ④防静电手套Anti-static gloves ⑤安全鞋Safety shoes |
| 3 | 加药作业 Dosing | 冷机房内化学药品添加 Chemical dosing in the chilling room | ①防护眼镜 Protective glasses ②耳塞或耳罩 Earplugs ③防化学手套Chemical-resistant gloves ④安全鞋Safety shoes |
| 4 | 焊接作业 Welding | 数据中心室外管道焊接 Welding of outdoor tubes | ①安全帽Safety helmet ②焊接眼护具 Eye protection ③反光背心 Reflective vest ④焊工防护手套 Heat-Resistant welding gloves |
| 5 | 电气作业 Electrical | 室内、室外电柜接线、维修 Wiring and maintenance of indoor and outdoor electrical cabinets | ①安全帽 Safety helmet ②反光背心 Reflective vest ③安全鞋 Safety shoes |
| 6 | 机械设备调试或测试作业 Mechanical testing | 消防泵启停测试、柴油发电机启停测试、风机启停产生 Fire pump start-stop test, diesel generator start-stop test, fan start-stop generation | ①耳塞或耳罩 Earplugs |
| 7 | 搬运作业 Handling | 铅酸电池搬运 Battery handling | ①安全鞋 Safety shoes |
| 8 | 切割作业 Cutting | 管道的切割 Cutting of pipes | ①安全帽 Safety helmet ②反光背心Reflective vest ③护目镜Protective glasses ④耳塞或耳罩Earplug ⑤安全鞋Safety shoes |
| 9 | 设备维修检测巡视 Equipment Maintenance and inspection | 在低矮的空间（如高处较狭小的管道间空间处）行走或作业，头部有可能碰撞到尖锐、坚硬的物体时。 When walking or working in a low space (such as a narrow space between pipes at a height), the head is likely to collide with a sharp, hard object. | ①安全帽Safety helmet ②反光背心Reflective vest ③安全带Safety belt ④安全鞋Safety shoes |

6.3.11劳动防护用品发放记录详见附件2。

Release records of labor protective equipment are detailed in Attachment 2.

## 6.4追踪溯源 Tracing

6.4.1数据中心应购置在最小贴码包装及运输包装上具有追踪溯源标识的劳动防护用品，该标识应能通过全国性追踪溯源系统实现追踪溯源。

The data center shall purchase labor protection equipment with traceability identification on the minimum sticker packaging and transportation packaging, which shall be traceable through the national traceability system.

6.4.2数据中心在采购劳动防护用品时，可通过产品和检验检测报告的追踪溯源标识，对产品实物信息和产品检验检测报告信息进行核实。

When purchasing labor protection articles, data centers can verify the physical information of products and the information of product inspection and testing reports through the tracking and traceability marks of products and inspection and testing reports.

## 6.5判废和更换 Rejection and replacement

6.5.1出现以下情况之一，数据中心应给予判废和更换新品；

In any of the following cases, the data center shall be condemned and replaced with new products.

- 劳动防护用品经检验或检查被判定不合格；

Labor protection articles are judged to be unqualified after inspection or inspection.

- 劳动防护用品超过有效期；

Labor protective articles have expired.

- 劳动防护用品功能已经失效；

The function of labor protective articles has failed.

- 劳动防护用品的使用说明书中规定的其他判废或更换条件。

Other conditions for disqualification or replacement stipulated in the instruction manual of labor protective articles.

6.5.2 被判废或被更换后的劳动防护用品不得再次使用。

After being disqualified or replaced, the labor protective articles shall not be used again.

6.5.3 变配电室绝缘安全用具及校验周期详见表2。

See Table 2 for details on insulation safety appliances and calibration cycles in the power distribution room.

表2 变配电室绝缘安全用具及校验周期

Table 2 Insulation safety appliances and calibration cycle of power distribution room

| 序号 No. | 器具 Tools | 项目 Items | 周期 Period |
| --- | --- | --- | --- |
| 1 | 电容型验电器 Capacitive electroscope | 启动电压试验 Starting voltage test | 1年 1 year |
|  |  | 工频耐压试验 Power frequency withstand voltage test | 1年 1year |
| 2 | 携带型短路接地线 Portable short-circuit grounding wire | 成组直流电阻试验 Group DC resistance test | ≤5年 ≤5 years |
|  |  | 操作棒的工频耐压试验 Power frequency voltage withstand test of operating rod | 5年 ≤5 years |
| 3 | 绝缘隔板 Insulation divider | 表面工频耐压试验 Surface power frequency withstand voltage test | 1年 1year |
|  |  | 工频耐压试验装置 Power frequency withstand voltage test device | 1年 1year |
| 4 | 绝缘夹钳 Insulation clamp | 工频耐压试验 Power frequency withstand voltage test | 1年 1year |
| 5 | 绝缘绳 Insulation rope | 工频耐压试验 Power frequency withstand voltage test | 半年 Half year |
| 6 | 绝缘杆 Insulation rod | 工频耐压试验 Power frequency withstand voltage test | 1年 1year |
|  |  | 绝缘部分工频耐压试验 Power frequency voltage withstand test of insulation part | 1年 1year |
|  |  | 电阻管泄露电流试验 Resistance tube leakage current test | 半年 Half year |
|  |  | 动作电压 Action voltage | 1年 1year |
| 7 | 绝缘罩 Insulation cover | 工频耐压试验 Power frequency withstand voltage test | 1年 1year |
| 8 | 绝缘胶垫 Insulation rubber pad | 工频耐压试验 Power frequency withstand voltage test | 1年 1year |
| 9 | 绝缘靴 Insulation boots | 工频耐压试验 Power frequency withstand voltage test | 半年 Half year |
| 10 | 绝缘手套 Insulation gloves | 工频耐压试验 Power frequency withstand voltage test | 半年 Half year |
| 参考标准：DB13/T 5614 变配电室安全管理规范 Reference standard: DB13/T 5614 Substation safety management code |  |  |  |

6.5.4 其他劳动防护用品（如安全帽、防护手套等）的使用周期根据产品说明而定。

The service cycle of other labor protective articles (such as safety hats, protective gloves, etc.) shall be determined according to the product instructions.

## 6.6 验证与监控 Verification and monitoring

6.6.1劳动防护用品的有效性应定期审查，并将结果传达给受影响的员工。 该审查应考虑以下因素：

The effectiveness of labor protective equipment should be reviewed regularly, and the results communicated to the affected employees. This review shall take into account the following factors:

- 过去几年的劳动防护用品有效性审查；

A review of the effectiveness of labor protective equipment in previous years.

- 与劳动防护用品有关的审核发现；

Audit findings related to labor protective equipment.

- 员工对劳动防护用品类型、用途等的反馈；

Feedback from employees on the types and uses of labor protective equipment.

- 政府相关部门（如应急管理局、卫健委等）执法活动；

Law enforcement activities of relevant government departments (such as emergency management Bureau, health commission, etc.).

- 伤害和疾病趋势；

Injury and disease trends.

- 法规要求。

Regulatory requirements.

6.6.2适用时，劳动防护用品管理可在数据中心内部审核或第三方审核过程中进行验证。

Where applicable, the management of labor protection products may be verified during the data center internal audit or third-party audit process.

## 6.7沟通与培训 Communication and training

6.7.1数据中心应制定劳动用品配备、使用及报废相关的培训计划和考核办法，并建立和保留培训和考核记录。

The data center shall develop training plans and assessment methods related to the equipment, use and scrapping of labor supplies, and establish and keep training and assessment records.

6.7.2数据中心应按计划定期对作业人员进行培训，培训内容至少应包括工作中存在的危害种类和法律法规、标准等规定的防护要求，本单位采取的控制措施，以及劳动防护用品的选择、防护效果、使用方法及维护、保养方法、检查方法等。

The data center shall regularly train the operators according to the plan, and the training content shall at least include the types of hazards existing in the work and the protection requirements stipulated by laws, regulations and standards, the control measures taken by the unit, and the selection, protection effect, use method and maintenance, maintenance method and inspection method of labor protection supplies.

6.7.3当有新员工入职，员工转岗，劳动防护用品配备发生变化、法律法规及标准发生变化等情况，需要培训时数据中心应及时进行培训。

When new employees are recruited, employees are transferred, labor protection equipment is changed, laws and regulations and standards are changed, etc., the data center shall conduct training in time.

6.7.4未按规定佩戴和使用劳动防护用品的作业人员，不得上岗作业。

Workers who do not wear and use labor protective equipment in accordance with regulations shall not be on duty.

6.7.5作业人员应熟练掌握劳动防护用品正确佩戴和使用方法， 数据中心应监督作业人员劳动防护用品的使用情况。

The operators should be proficient in the correct wearing and use of labor protective equipment, and the data center should supervise the use of labor protective equipment.

6.7.6在使用劳动防护用品前，作业人员应对劳动防护用品进行检査（如外观检査、适合性检査等），确保劳动防护用品能够正常使用。

Before using the labor protective articles, the operators should check the labor protective articles (such as appearance check, suitability check, etc.) to ensure that the labor protective articles can be used normally.

6.7.7数据中心应按照产品使用说明书的有关内容和要求，指导并监督劳动防护用品使用人员对在用的劳动防护用品进行正确的日常维护和使用前的检査，对必须由专人负责的，应指定受过培训的合格人员负责日常检查和维护。

The data center shall, in accordance with the relevant contents and requirements of the product instruction manual, guide and supervise the personnel using the labor protective articles to carry out the correct daily maintenance and pre-use inspection of the labor protective articles in use. For those who must be responsible by special personnel, the trained and qualified personnel shall be designated to take charge of the daily inspection and maintenance.

- 附件 Attachments

- IF-PJ-EHS-1601：劳动防护用品配备标准 Personal Protection Equipment Issue Standard

- IF-PJ-EHS-1602：劳动防护用品发放记录 Personal Protection Equipment Issue Record