防雷、防静电装置安全管理制度

Safety Management System for Lightning Protection and Anti-static Devices

内部使用

在使用前，请和文档编写人员确认本文档为最新版本。

未经上海暻熠数据科技有限公司、上海暻耀网络技术有限公司书面许可，其它任何机构或个人不可传阅、引用或复制本文件的内容。

Internal use

Before using, check with the documentation writer to make sure this document is the latest version.

Without the written permission of Shanghai Jingyi Data Technology Co., Ltd., Shanghai Jingyao internet Technology Co., Ltd., no other organization or individual is allowed to circulate, quote or copy the content of this document.

| 文件编号Documents | IP-PJ-EHS-37 |
| --- | --- |
| 版 本Edition | V1.0 |
| 文件维护部门File maintenance department | 上海浦江数据中心 |
| 会签部门Document Signing department | 上海浦江数据中心 |
| 执行范围Scope of execution | 上海浦江数据中心 |

文件修订记录

Document revision record

| 版本号 Edition | 版本日期 Date | 修订内容 Revised Content | 修订人员 Revision personnel | 核准员 Approver | 备注 Remarks |
| --- | --- | --- | --- | --- | --- |
| V1.0 | 2025-04-17 | 首次修订 | 楚靖岳 | 陆磊 |  |

目录Content

1 目的Purpose	4

2 适用范围Scope of application	4

3 规范性引用文件Normative References	4

4 术语和定义Terms and Definitions.	4

5 职责Duty	5

5.1 EHS管理负责人EHS officer	5

5.2 各部门/岗位/业务线Departments/Positions/Business Lines	6

6 程序Procedure	6

6.1 防雷技术措施Lightning protection technical measures	6

6.2 防雷装置Lightning protection device	6

6.3 独立避雷针系统Independent lightning rod system	8

6.4 建筑物、构筑物的防雷Lightning protection of buildingsandstructures	8

6.5 防雷区域防雷装置的管理Management of lightning protection devices in lightning protection areas	9

6.6 接地保护Grounding protection	10

6.7 防静电装置Anti-static device	10

6.8 检测要求Testing requirements	11

附件 Attachment	11

- 目的objective

为加强和规范上海暻熠数据科技有限公司、上海暻耀网络技术有限公司（以下简称“上海浦江数据中心”）的防雷、防静电接地装置的有效性，减少因雷、电引发火灾、爆炸等事故发生的可能性，特制订本制度。

In order to strengthen and standardize the effectiveness of the lightning protection and anti-static grounding devices of Shanghai Jingyi Data Technology Co., Ltd., Shanghai Jingyao internet Technology Co., Ltd.. (hereinafter referred to as "SHANGHAI Pujiang Data Center"), and reduce the possibility of fire, explosion and other accidents caused by lightning and electricity, this system is specially formulated.

- 适用范围Scope of application

适用于上海浦江数据中心所有易遭受雷击区域的建筑物、构筑物，以及雷电波侵入室内可能造成危害的场所及设备。

It is suitable for all buildings and structures in areas prone to lightning strikes in SHANGHAI PUJIANG Data Center, as well as places and equipment that may cause harm due to lightning waves intruding into the room.

- 规范性引用文件Normative references

GB 50057   建筑物防雷设计规范

Code for lightning protection design of buildings

GB50169    电气装置安全工程接地装置施工及验收规范

Code for construction and acceptance of grounding devices for electrical

installation safety engineering

GB/T50065  交流电气装置的接地设计规范

Grounding design code for AC electrical installations

- 术语和定义Terms and Definitions

  - 接地极Grounding electrode

埋入地中并直接与大地接触的金属导体称为接地极，分为水 平接地极和垂直接地极。  The metal conductor that is buried in the ground and in direct contact with the earth is

called the grounding electrode, which is divided into a horizontal grounding electrode and a vertical direct grounding electrode.

  - 接地线（导体）Grounding wire (conductor)

电气设备、接闪器的接地端子与接地极连接用的，在正常情况 下不载流的金属导体。    The grounding terminal of electrical equipment and flash receiver is connected with the

grounding electrode, and is not current-carrying metal conductor under normal conditions.

  - 接闪器Flash receiver

接受雷电闪击装置的总称，包括避雷针、避雷带、避雷线、避雷 网以及金属屋面、金属构件等。

The general term for receiving lightning strike devices, including lightning rods,

lightning belts, lightning cables, lightning nets, metal roofs, metal components, etc.

  - 接地装置Grounding device

接地极和接地线的总和。

The sum of the ground electrode and the ground wire.

  - 接地Earthing

将电力系统或建筑物电气装置、设施、过电压保护装置用接地 线与接地极连接。

The electrical installations, facilities, and overvoltage protection devices of the power

system or buildings are connected with the grounding electrode with the grounding wire.

  - 接地电阻Ground resistance

接地阻扰的实部，工频时为工频接地电阻。

The actual part of the ground resistance，when the power frequency is the power

frequency ground resistance.

  - 保护接地Protective grounding

电气装置的金属外壳、配电装置的构架和线路杆塔等，由于绝 缘损坏有可能带电，为防

止其危及人身和设备的安全而设的接地。

The metal shell of the electrical installation, the frame of the power distribution device

and the line tower, etc., may be charged due to the accidental damage, and the grounding is set up to prevent it from endangering the safety of people and equipment.

- 职责Duty

  - EHS管理负责人EHS officer

    - 负责组织本制度的制定、修订与运行。

Responsible for organizing the formulation, revision and operation of this system.

    - 负责对防雷、防静电设施的维护和保养，并定期请有资质的专业单位进行检测。

Responsible for the maintenance and maintenance of lightning protection and anti-static facilities, and regularly invite qualified professional units to conduct testing

  - 各部门/岗位/业务线Departments/ Positions/Business Lines

    - 认真执行本管理制度要求。

Conscientiously implement the requirements of this management system.

    - 负责本单位防雷、防静电设施的日常维护工作。

Responsible for the daily maintenance of lightning protection and anti-static facilities of the unit.

- 程序Procedure

  - 防雷技术措施Lightning protection technical measures

    - 防雷技术措施须经安全设计与验算，使其保护范围有效。

Lightning protection technical measures must be subject to safety design and verification to make their protection scope effective.

    - 正确地设计、验算和合理地布置、安装防雷装置。

Correctly design, check and reasonably arrange and install lightning protection devices.

    - 保护空间范围至少应满足被保护半径和被保护的高度这两个方面。应防雷直击、防雷侧击，防雷电波浸人，防雷反击、防地电位升等。每年在雷雨李节前，进行动态安全评价检查与验算，确保保护范围的有效性。

The scope of the protected space should at least meet the two aspects of the protected radius and the protected height. It should be protected from direct lightning strikes, lightning side attacks, lightning protection and radio wave immersion, lightning protection counterattack, and ground potential rise. Every year, before the Thunderstorm Li Festival, dynamic safety evaluation inspection and calculation are carried out to ensure the effectiveness of the protection scope.

    - 进行安全设计与验算,应达到建筑物和构筑物的防雷分类和电气设备过电压保护的要求，且注意保护方式和计算公式的选择。

The safety design and verification should meet the requirements of lightning protection classification of buildings and structures and overvoltage protection of electrical equipment, and pay attention to the selection of protection methods and calculation formulas.

  - 防雷装置Lightning protection device

    - 接闪器Flash receiver

- 避雷针一般采用圆钢或焊接钢管制成，且应镀锌或涂漆。针长1m以下的，圆钢为

φ12mmm,钢管为φ20mm。针长1-2m的，圆钢为φ16mm,钢管为φ25mm。烟图顶上

的针，圆钢为φ20mm，钢管为φ40mm；

Lightning rods are generally made of round steel or welded steel pipes and should be galvanized or painted. If the needle length is less than 1m, the round steel is φ12mm, steel pipe φ20mm. If the needle length is 1-2m, the round steel is φ16mm, and the steel pipe is φ25mm. The needle on the top of the smoke diagram is φ20mm for round steel and φ40mm for steel pipe;

- 避雷网和避雷带一般采用圆钢或扁钢。圆钢直径不小于8mm ，避雷扁钢截面不小于

48mm2，厚度不小于4mm。避雷线一般采用不小于35mm2镀锌钢绞线；

Lightning nets and lightning belts are generally made of round steel or flat steel. The diameter of the round steel is not less than 8mm, the cross-section of the lightning protection flat steel is not less than 48mm2, and the thickness is not less than 4mm. The lightning protection wire is generally not less than 35mm2 galvanized steel strand.

- 当烟囱上采用避雷环时，其圆钢直径不应小于12mm，扁钢截面不应小于100mm2，其

厚度不小于4mm。

When the lightning ring is used on the chimney, the diameter of the round steel should not be less than 12mm, and the cross-section of the flat steel should not be less than 100mm2 The thickness is not less than 4mm.

    - 引下线Down leads

- 引下线应沿建筑物、构筑物外墙敷设，并经最短路径接地。金属构件，如消防梯等可作

引下线，但其所有部件均应连成电气通路；

The down conductor should be laid along the exterior wall of the building or structure and grounded through the shortest path. Metal components, such as fire ladders, can be used as down wires, but all their components should be connected to form electrical paths.

- 引下线尺寸圆钢φ8mm，扁钢截面48mm2，厚度4mm。装置在烟囱上的引下线，圆钢

φ12mm，扁钢截面100mm2，厚度4mm；

The size of the down conductor is φ8mm, the cross-section of the flat steel is 48mm2, and the thickness is 4mm. Down-lead wire installed on the chimney, round steel φ12mm, flat steel cross-section 100mm2, thickness 4mm.

    - 接地装置Grounding device

- 避雷针（带）与引下线的接地装置连接应采用焊接。整体防雷装置应保证完好的电气通

路和连接的可靠性（包括跨接线和过度伸缩缝的处理等）。

The connection between the lightning rod (belt) and the grounding device of the down conductor should be welded. The overall lightning protection device should ensure the integrity of the electrical paths and the reliability of the connection (including the treatment of jumper wires and over-expansion joints, etc.).

- 防雷接地电阻实际检测一般不超过10欧，特殊情况遵从安全设计值，允许与其他接地装

置共用时，满足其中最低的要求。

The actual detection of lightning protection grounding resistance is generally not more than 10 ohms, and the safety design value is followed in special cases, and it is allowed to be shared with other grounding devices to meet the minimum requirements.

  - 独立避雷针系统Independent lightning rod system

    - 独立避雷针与其他接地网、金属物体间距至少不小于3m。

The distance between the independent lightning rod and other grounding grids and metal objects shall not be less than 3m.

    - 严禁在装有避雷针、避雷线的构筑物上架设通讯线、广播线或低压线。利用照明灯塔作为独立避雷针支柱时，照明电源线必须采用铅皮电缆或传入铁管，并将其至少埋入地下15m以上，埋深0.6-0.8m，金属护层或金属管必须接地。

It is strictly forbidden to erect communication lines, broadcasting lines or low-voltage lines on structures equipped with lightning rods and lightning cables. When using the lighting tower as an independent lightning rod pillar, the lighting power cord must be made of lead cable or incoming iron pipe, and it must be buried at least 15m underground, buried at a depth of 0.6-0.8m, and the metal sheath or metal pipe must be grounded.

    - 独立的避雷针不应设在人员通行的地方。

Stand-alone lightning rods should not be located in areas of human traffic.

  - 建筑物、构筑物的防雷Lightning protection of buildings and structures

    - 建筑物、构筑物的防雷应有防反击、侧击等技术措施；与道路或建筑物的出入口有防止跨步电压触电的措施；路线应有防雷电波侵入的技术措施。

The lightning protection of buildings and structures should have technical measures such as anti-counterattack and side strike; There are measures to prevent step voltage electrocution at the entrances and exits of roads or buildings; The route should have technical measures to prevent the intrusion of lightning waves.

    - 金属物或线路与防雷装置不相连时，与引下线之间的距离一般不得小于5m。如果达不到，则应把他们直接连接成等电位体或者与避雷器连接。

When the metal object or line is not connected to the lightning protection device, the distance between the metal object or the line and the down conductor shall generally not be less than 5m. If this is not possible, they should be connected directly to an equipotential or to a lightning arrester.

    - 对于有防爆要求的建筑物、构筑物，钢制气罐（壁厚不小于4mm）内外的金属物品，管道、线路应连接成等电位并接地。

For buildings and structures with explosion-proof requirements, and metal objects inside and outside steel gas tanks (wall thickness not less than 4mm), pipes and lines should be connected to equipotential and grounded.

    - 线路应有防雷电波侵入措施：可采取在进户处专设避雷器，过电压保护器具等办法，或将其金属部位埋地长度不小于15m等。所有防雷装置及其接地装置与道路或建筑物的出入口距离应大于3m，当小于3m时，应采取均压措施或铺设卵石、沥青地面（50-80mm厚沥青层，其宽度超过接地装置2m），并由防止跨步电压触电的安全色标作警示。

The line should have lightning protection measures: lightning arresters, overvoltage protection appliances and other methods can be adopted at the entrance to the house, or the length of the metal part buried is not less than 15m. The distance between all lightning protection devices and their grounding devices and the entrances and exits of roads or buildings should be greater than 3m, and when it is less than 3m, pressure equalization measures should be taken or pebbles and asphalt floors should be laid (50-80mm thick asphalt layer, the width of which exceeds 2m of grounding devices), and the safety color code to prevent step voltage electric shock as a warning.

  - 防雷区域防雷装置的管理Management of lightning protection devices in lightning protection areas

    - 对防雷区域和防雷装置定期进行预防性检查、评价和检测

Preventive inspections, evaluations and inspections are carried out on a regular basis for lightning protection areas and lightning protection devices.

    - 定期检测实验：对接地装释、阀型避雷器等每年应在雷雨季节前检测，并有专业检测报告和数据。

Regular testing experiments: grounding loading and release, valve-type arresters, etc. should be tested before the thunderstorm season every year, and there should be professional test reports and data.

    - 经常性检测：对各种防雷装置应按规范标准要求检查整体和器件情况，例如，连接点有无裂纹。引下线上有无闪络或烧损痕迹、腐蚀、锈蚀以及与相邻导体的安全距离情况等。

Frequent inspection: The overall and device conditions of various lightning protection devices should be checked according to the requirements of the specifications and standards, for example, whether there are cracks in the connection points. Whether there are flashover or burn marks, corrosion, rust and safety distance from adjacent conductors on the down conductor.

    - 对于利用原有防雷装置的房屋区域，是否有新、改、扩建项目的建筑物、构筑物或有新的易燃易爆场所，并应重新验算其保护范围。

For the housing area that uses the original lightning protection device, whether there are new, renovated or expanded buildings, structures or new flammable and explosive places, and the scope of protection should be re-checked.

    - 有关检测、检查资料，定期检测报告完整有效。

The relevant testing and inspection data and regular testing reports are complete and valid.

  - 接地保护Grounding protection

    - 电气设备的金属部分,除加有规定外，均应接地或接零。

The metal parts of electrical equipment, unless otherwise specified, shall be grounded or zeroed.

    - 地装置的设计应符合《交流电气装置的接地设计规范》（GB/T 50065）。

The design of the ground installation shall conform to the Code for Grounding Design of AC Electrical Installations (GB/T 50065).

    - 通用电器设备的保护接地线必须采用多股裸铜线，并符合截面和机械强度要求,利用串接的金属构件、管道作为接地线时，应在其串接部分另焊金属跨接线。

The protective grounding wire of general electrical equipment must be made of multi-strand bare copper wire, and meet the requirements of cross-section and mechanical strength.

    - 接地装置的接地电阻应符合以下规定：

The grounding resistance of the grounding device shall comply with the following provisions:

- 大接地短路电流系统的电力设备,接地电阻不应超过5.2Ω。

For power equipment with large ground short-circuit current system, the ground resistance should

not exceed 5.2Ω.

- 小接地短路电流系统的电力设备,接地电阻不应超过10Ω。

For power equipment with small ground short-circuit current systems, the ground resistance should

not exceed 10Ω.

- 低压电力设备的接地电阻不应超过4Ω,总容量在100KVA以下的变压器、低压电力网接

阻不应超10Ω。

The grounding resistance of low-voltage power equipment should not exceed 4Ω, and the total capacity of transformers and low-voltage power networks with a total capacity of less than 100KVA should not exceed 10Ω.

- 防静电的接地装置可与防感应雷和电气设备的接地装置共同设置，其接地电阻值应符合

应雷和电气设备接 地的规定，只作防静电的接地装置，每一次接地体的接地电阻值不应

大于100Ω。

The anti-static grounding device can be set together with the grounding device of anti-induction lightning and electrical equipment, and its grounding resistance value should be in accordance with it In response to the provisions of lightning and electrical equipment grounding, only the grounding device for anti-static electricity, and the grounding resistance value of each grounding body should not be >100Ω.

  - 防静电装置Anti-static device

    - 在易燃易爆场所、有产生静电导致电击危险的场所、有产生静电导致其他事故的场所采取静电防护措施,对各种静电装置应定期维修保养和检测。

In flammable and explosive places, places where there is a risk of electric shock caused by static electricity, and places where static electricity causes other accidents, electrostatic protection measures should be taken, and various electrostatic devices should be regularly repaired and tested.

    - 防静电用品及器材主要技术性能指标应符合下列要求:

The main technical performance indicators of anti-static products and equipment shall meet the following requirements:

- 导静电胶板其对地电阻值应为5.0×104－-1.0×108Ω。

The resistance value of the electrostatic conductive rubber plate to the ground should be

5.0×104—1.0×108Ω.

- 人体静电测试仪检测范围0-∞Ω,测量值误差不大于±10％。

The detection range of the human electrostatic tester is 0-∞Ω, and the error of the

measured value is not more than ±10%.

- 工作服的摩擦带电量应小于0.5UC/件，服装布料的摩擦电位应小于1UC/M2，摩擦起电

电位应小于500V。

The friction belt of the work clothes should be less than 0.5UC/piece, and the friction potential of the clothing fabric should be less than 1UC/M2, and the friction should be electrified The potential should be less than 500V.

  - 检测要求Testing requirements

    - 防雷接地装置每年雷雨季节前应检测一次，防静电接地 装置每年干燥季节应检测一次，防静电地面一年检测两次，发现不合格应立即处理。

The lightning protection grounding device should be tested once a year before the thunderstorm season, the anti-static grounding device should be tested once a year in the dry season, and the anti-static ground should be tested twice a year, and it should be dealt with immediately if it is found to be unqualified.

    - 由EHS管理负责人联系专门检测机构进行检测，并保留合格记录。

The person in charge of EHS officer shall contact a specialized testing institution for testing and keep a record of qualification.

- 附件attachment

无None