消防安全管理制度

Fire Safety Management System

内部使用

在使用前，请和文档编写人员确认本文档为最新版本。

未经上海暻熠数据科技有限公司、上海暻耀网络技术有限公司书面许可，其它任何机构或个人不可传阅、引用或复制本文件的内容。

Internal use

Before using, check with the documentation writer to make sure this document is the latest version.

Without the written permission of Shanghai Jingyi Data Technology Co., Ltd., Shanghai Jingyao internet Technology Co., Ltd., no other organization or individual is allowed to circulate, quote or copy the content of this document.

| 文件编号Documents | IP-PJ-EHS-38 |
| --- | --- |
| 版 本Edition | V1.0 |
| 文件维护部门File maintenance department | 上海浦江数据中心 |
| 会签部门Document Signing department | 上海浦江数据中心 |
| 执行范围Scope of execution | 上海浦江数据中心 |

文件修订记录

Document revision record

| 版本号 Edition | 版本日期 Date | 修订内容 Revised Content | 修订人员 Revision personnel | 核准员 Approver | 备注 Remarks |
| --- | --- | --- | --- | --- | --- |
| V1.0 | 2025-06-25 | 初版发布 | 楚靖岳 | 陆磊 |  |

目录Content

1 目的Purpose	4

2 适用范围Scope of application	4

3 规范性引用文件Reference documents	4

4 术语和定义Terms and definitions	5

5 职责Responsibility	7

5.1 消防维保人员Fire maintenance personnel	7

5.2 消防责任人 Fire Protection Responsible Person	13

5.3 防火巡查人员（安保/运维技术员）Fire patrol personnel (security/operation and maintenance technicians)	  14

5.4 消防控制室人员 Fire control room personnel	15

5.5 消防管理负责人 Fire Management Manager	19

6 管理要求Management requirements	20

6.1 人员管理staff management	20

6.1.1消防安全责任人Fire safety responsible person	20

6.2 微型消防站管理Micro fire station management	22

6.3消防法律责任Fire legal responsibility	23

6.4 消防设备设施管理Fire equipment and facility management	24

6.3 消防安全重点部位管理Management of key fire safety areas	27

6.4 动火作业及防火Hot work and fire prevention	28

6.5 消防安全检查及隐患整改Fire safety inspection and hidden danger rectification	31

6.6 消防演习与培训Fire drills and training	32

7 附件Attachments	36

1 目的Purpose

本制度旨在建立上海暻熠数据科技有限公司、上海暻耀网络技术有限公司（以下简称“上海浦江数据中心”）消防安全管理流程。目标包括确保遵守国家和地方法律法规、国外相关法规、客户要求以及万国数据中心内部要求，确保消防安全管理合规，降低运营风险，并促进持续改进。

This system aims to establish the fire safety management process for Shanghai Jingyi Data Technology Co., Ltd., Shanghai Jingyao internet Technology Co., Ltd.. (hereinafter referred to as "SHANGHAI Pujiang Data Center"). The objectives include ensuring compliance with national and local laws and regulations, relevant foreign regulations, customer requirements, and internal requirements of the Universal Data Center, ensuring compliance with fire safety management, reducing operational risks, and promoting continuous improvement.

2 适用范围Scope of application

适用于上海浦江数据中心消防安全管理，以及所有与消防有关事项的管理职能部门。

Applicable to the fire safety management of SHANGHAI PUJIANG Data Center and all management functional departments related to fire safety matters.

3 规范性引用文件Reference documents

《中华人民共和国消防法》（2021年修订）

Fire Protection Law of the People's Republic of China (Revised in 2021)

《机关、团体、企业、事业单位消防安全管理规定》（公安部令第 61 号）

Regulations on Fire Safety Management of Government Agencies, Organizations, Enterprises, and Institutions (Order No. 61 of the Ministry of Public Security)

《建设工程消防设计审查验收管理暂行规定》（住房和城乡建设部令第51号）

Interim Provisions on the Management of Fire Protection Design Review and Acceptance of Construction Projects (Order No. 51 of the Ministry of Housing and Urban Rural Development)

《建设工程消防监督管理规定》（公安部令第106号）

Regulations on Fire Supervision and Management of Construction Projects (Order No. 106 of the Ministry of Public Security)

《上海市消防条例》（2020年3月19日修订）

Shanghai Fire Protection Regulations (revised on March 19, 2020)

《上海市建筑消防设施管理规定》（2022年3月1日实施）

Regulations on the Management of Building Fire Protection Facilities in Shanghai (implemented on March 1, 2022)

《上海市消防安全责任制实施办法》（2020年1月22日修订）

Implementation Measures for Shanghai Fire Safety Responsibility System (Revised on January 22, 2020)

## 《关于抓紧建立和认真落实建筑消防设施检查维修保养管理制度的通知》（1996-03-18起施行）

Notice on Urgently Establishing and Seriously Implementing the Management System for Inspection, Maintenance and Repair of Building Fire Protection Facilities (implemented from March 18, 1996)

TSG 23—2021《气瓶安全技术规程》

TSG 23-2021 Technical Regulations for Gas Cylinder Safety

GB50263－2007《气体灭火系统施工及验收规范》

GB50263-2007 Code for Construction and Acceptance of Gas Fire Extinguishing Systems

GB 50016建筑设计防火规范

GB 50016 Code for Fire Protection Design of Buildings

GB 29837火灾探测报警产品的维修保养与报废

GB 29837 Maintenance and Scrapping of Fire Detection and Alarm Products

GB 50116 火灾自动报警系统设计规范

GB 50116 Design Specification for Automatic Fire Alarm System

GB 25201 建筑消防设施的维护管理

GB 25201 Maintenance and Management of Building Fire Protection Facilities

GB 55036 消防设施通用规范

GB 55036 General Specification for Fire Protection Facilities

GB 50166 火灾自动报警系统施工及验收规范

GB 50166 Code for Construction and Acceptance of Automatic Fire Alarm System

GB 50444 建筑灭火器配置验收及检查规范

GB 50444 Code for Acceptance and Inspection of Fire Extinguisher Configuration in Buildings

GB 25506 消防控制室通用技术要求

GB 25506 General Technical Requirements for Fire Control Rooms

GB 1530 消防安全标志设置要求

GB 1530 Requirements for Setting Fire Safety Signs

GB 13495.1 消防安全标志 第1部分：标志

GB 13495.1 Fire Safety Signs Part 1: Signs

XF 480.1-6   消防安全标志通用技术条件

XF 480.1-6 General Technical Conditions for Fire Safety Signs

GB 50174-2017   数据中心设计规范

GB 50174-2017 Data Center Design Specification

GB 50261-2017自动喷水灭火系统施工及验收规范

GB 50261-2017 Code for Construction and Acceptance of Automatic Sprinkler Systems

4 术语和定义Terms and definitions

4.1主动消防系统Active fire protection system

数据中心的主动消防系统是指能够自行检测、报警、灭火或控制火势发展的消防设备和系统，与被动消防系统相对应。 主动消防系统能够在火灾初期自动或手动启动，对火源进行扑灭或控制火势发展，有效避免火灾的扩散和蔓延，保护人员和财产安全，主要包括火灾自动报警系统、消火栓系统、自动喷淋系统、防排烟系统。

The active fire protection system in data centers refers to fire equipment and systems that can detect, alarm, extinguish, or control the spread of fire on their own, corresponding to passive fire protection systems. The active fire protection system can be automatically or manually activated in the early stages of a fire to extinguish or control the spread of the fire, effectively avoiding the spread of the fire and protecting personnel and property safety. It mainly includes fire automatic alarm system, fire hydrant system, automatic sprinkler system, and smoke control system。

4.2消防Fire protection

火灾预防和灭火救援等的统称。

The general term for fire prevention and firefighting and rescue.

4.3火灾分类Fire classification

根据可燃物的类型和燃烧特性，按标准化的方法对火灾进行的分类。

注：GB/T 4968规定了具体的火灾分类。

Classify fires according to standardized methods based on the types of combustibles and combustion characteristics.

Note: GB/T 4968 specifies specific fire classifications.
4.4火灾隐患Fire potential
     可能导致火灾发生或火灾危害增大的各类潜在不安全因素。

Various potential unsafe factors that may lead to the occurrence of fire or an increase in fire hazards.

4.5消防安全标志Fire safety sign
      由表示特定消防安全信息的图形符号、安全色、几何形状（或边框）等构成，必要时辅以文字或方向指示的安全标志。

注：GB 13495规定了具体的消防安全标志。

A safety sign composed of graphic symbols, safety colors, geometric shapes (or borders), etc. that represent specific fire safety information, supplemented by text or directional instructions when necessary.

Note: GB 13495 specifies specific fire safety signs.

4.6消防设施Fire facility

专门用于火灾预防、火灾报警、灭火以及发生火灾时用于人员疏散的火灾自动报警系统、自动灭火系统、消火栓系统、防烟排烟系统以及应急广播和应急照明、防火分隔设施、安全疏散设施等固定消防系统和设备。

Specially used for fire prevention， fire alarm, fire extinguishing , as well as fire automatic alarm system, automatic fire extinguishing system, fire hydrant system, smoke control and exhaust system, emergency broadcasting and emergency lighting, fire separation facilities, safety evacuation facilities and other fixed fire protection systems and equipment for personnel evacuation in case of fire.

4.7 局部应用灭火系统Local application extinguishing system
     向保护对象以设计喷射率直接喷射灭火剂，并持续一定时间的灭火系统。

A fire extinguishing system that directly sprays fire extinguishing agent at a designed spray rate onto the protected object for a certain period of time.
4.8初期火灾Initial fire

早期的火灾，此时期的火灾是可以通过标准的灭火器或等效的过程扑灭的。

Early fires during this period can be extinguished using standard fire extinguishers or equivalent processes.

4.9消防安全重点部位Key fire safety areas

应当将容易发生火灾、一旦发生火灾可能严重危及人身和财产安全以及对消防安全有重大影响的部位确定为消防安全重点部位，如变配电室、消防控制室等。

Areas that are prone to fire, may seriously endanger personal and property safety in the event of a fire, and have a significant impact on fire safety should be identified as key fire safety areas, such as transformer and distribution rooms, fire control rooms, etc.

4.10建筑消防设施Building fire protection facilities

建筑物、构筑物中设置的用于报警、灭火、人员疏散、防火分隔、灭火救援行动等设施的总称。

The general term for facilities set up in buildings and structures for alarm, fire extinguishing, personnel evacuation, fire separation, firefighting and rescue operations, etc.

4.11消防控制室Fire control room

设有专门装置以接受、显示、处理火灾报警信号，控制消防设施的房间。

A room equipped with specialized devices to receive, display, and process fire alarm signals, and control fire-fighting facilities.

5 职责Responsibilities

## 5.1 消防维保人员Fire maintenance personnel

5.1.1消防维保是消防系统发挥正常功能的前提保障，依照国家《火灾自动报警系统施工及验收规范》、《自动喷水灭火系统施工及验收规范》、《建筑消防设施检测技术规程》、《消防控制室通用技术要求》等规范，结合甲方的设备实际和管理要求，以使整个维保工作系统化、规范化，使整个系统始终处于良好的运行状态。消防设施维护保养是以“预防为主，防消结合”为宗旨。

Fire maintenance is a prerequisite guarantee for the normal functioning of the fire protection system. In accordance with national standards such as the "Code for Construction and Acceptance of Automatic Fire Alarm Systems", "Code for Construction and Acceptance of Automatic Sprinkler Systems", "Technical Regulations for Testing Building Fire Protection Facilities", and "General Technical Requirements for Fire Control Rooms", combined with the actual equipment and management requirements of Party A, the entire maintenance work is systematized and standardized to ensure that the entire system is always in good operating condition. The maintenance of fire-fighting facilities is based on the principle of "prevention first, combination of prevention and control".

5.1.2根据公安部《关于抓紧建立和认真落实建筑消防设施检查维修保养管理制度的通知》的要求，为保证大楼内的消防设施正常运行，确保大楼的人身和财产安全，依靠现有的高科技联网平台，拟制定该大楼消防设施的维修、保养服务方案如下：

According to the requirements of the "Notice on Establishing and Seriously Implementing the Management System for Inspection, Maintenance and Repair of Building Fire Protection Facilities" issued by the Ministry of Public Security, in order to ensure the normal operation of fire protection facilities in the building and ensure the personal and property safety of the building, relying on the existing high-tech networking platform, the maintenance and repair service plan for the fire protection facilities in the building is proposed as follows:

5.1.2.1消防设施维护、维修范围Scope of maintenance and repair of fire-fighting facilities

火灾自动报警系统的维护、维修范围包括The maintenance and repair scope of the automatic fire alarm system includes:

a)火灾自动报警系统

Automatic fire alarm system

b)自动喷水灭火系统；

Automatic sprinkler fire extinguishing system;

c)气体灭火系统；

Gas fire extinguishing system;

d)消火栓系统；

Fire hydrant system;

e)消防联动设备的维护维修负责到消防联动设备的接口；

The maintenance and repair of fire linkage equipment is responsible for the interface

of the fire linkage equipment;

f)消防报警线路和消防联动线路及消防联动电源线路、管路出现问题包括短路、断路。

Problems with fire alarm lines, fire linkage lines, fire linkage power lines, and pipelines include short circuits and open circuits.

5.1.2.2消防系统中各子系统的服务范围Service scope of each subsystem in the fire protection system

a)火灾自动报警系统

Automatic fire alarm system

a)-1对火灾报警系统作定期检查和试验

Regularly inspect and test the fire alarm system.

- 对火灾报警控制器的各功能进行试验。

Test the various functions of the fire alarm controller.

- 采用专用检测仪器分期分批试验探测器的动作及确认灯显示。

Use specialized testing instruments to conduct phased and batch testing of

detector actions and confirm the display of lights.

-  每年对备用电源进行1-2次充放电试验，1-3次主电源和备用电源自动切换试

验。

Conduct 1-2 charge and discharge tests on the backup power supply and 1-3

automatic switching tests between the main and backup power supplies

annually.

a)-2对消防系统联动设备作定期检查和试验。

Regularly inspect and test the linkage equipment of the fire protection system.

- 每年对防排烟设备、防火卷帘门等控制设备做消防联动试验两次。

Conduct fire linkage tests twice a year on control equipment such as smoke

exhaust equipment and fire-resistant rolling shutter doors.

- 每年对火灾事故广播进行消防联动试验两次。

Conduct fire linkage tests twice a year on fire accident broadcasts.

- 每年对电梯进行强制停于首层消防联动试验两次。

Conduct two mandatory fire linkage tests on elevators stopping at the first floor

every year.

- 每年对消防通讯设备在消防控制室进行对讲通话试验两次。

Conduct intercom communication tests on fire communication equipment twice

a year in the fire control room.

- 每年进行强制切断非消防电源消防联动试验两次。

Conduct mandatory disconnection of non fire power supply and fire linkage test twice a year.

a)-3 对火灾自动报警系统控制线路及联动线路的故障进行维修。

Repair the faults in the control and linkage circuits of the automatic fire alarm

system.

a)-4对火灾自动报警系统的故障进行维修。

Repair the malfunction of the automatic fire alarm system.

a)-5对火灾自动报警系统的消防通讯线路、消防主机电源检查及消防主机接地线路的故障的检查及维修。

Inspection and maintenance of fire communication lines, fire host power supply,

and fire host grounding lines for automatic fire alarm systems.

b) 消火栓系统Fire hydrant system

b)-1 每月对消防泵进行启动运转试验，并对消防泵进行消火栓按钮联动启泵试验。

Conduct monthly start-up and operation tests on fire pumps, and conduct fire

hydrant button linkage start-up tests on fire pumps.

b)-2每月对系统上所有的控制阀门进行检查，保证控制阀门处于正常工作状态。

Check all control valves on the system every month to ensure they are in normal

working condition.

b)-3每月对消火栓进行检查，发现问题及时处理。

Inspect fire hydrants monthly and promptly address any issues found.

b)-4每季度对最不利点消火栓进行静压压力试验。

Conduct static pressure tests on the most unfavorable fire hydrants every

quarter.

b)-5每半年对室内消火栓箱内的水枪、水带等设备进行检查，发现问题及时通报用户。

Inspect the water guns, hoses, and other equipment inside the indoor fire

hydrant box every six months, and promptly report any problems to users.

b)-6每年对水泵接合器的接口及附件进行检查。

Inspect the interface and accessories of the water pump adapter annually.

b)-7每年抽查消火栓的出水情况对重点部位的消火栓每年进行出水检查。

Conduct annual spot checks on the water output of fire hydrants, and inspect

the water output of fire hydrants in key areas every year.

c) 自动喷水灭火系统automatic sprinkler system

c)-1 每月对水源控制阀、报警阀组进行检查，保证系统各种阀门处于工

作状态。

Inspect the water source control valve and alarm valve group monthly to ensure

that all valves in the system are in working condition.

c)-2每月对喷淋水泵进行启动运转试验一次。

Perform a start-up test on the sprinkler water pump once a month.

c)-3每月对电磁阀作启动试验一次，动作失常时马上通知消防工程师及时更换。

Perform a start-up test on the solenoid valve once a month, and promptly notify

the fire engineer to replace it if it malfunctions.

c)-4 每月对喷头进行外观检查，发现有不正常的喷头及时更换，当喷头上有异物时及

时清除。

Conduct a monthly visual inspection of the nozzle, replace any abnormal

nozzles promptly, and remove any foreign objects from the nozzle in a timely

manner.

c)-5 每季度对湿式报警阀旁的放水试验阀进行泄水试验，验证湿式报警阀的供水能

力。

Conduct quarterly drainage tests on the water release test valve next to the wet

alarm valve to verify its water supply capacity.

c)-6每半年利用末端试水装置对水流指示器进行试验。

Every six months, the end water testing device is used to test the water flow

indicator.

c)-7每年对水泵接合器的接口及附件进行检查并进行维护。

Inspect and maintain the interface and accessories of the water pump adapter

annually.

c)-8 每年对消防水池，消防水箱及消防气压给水设备的消防储水位及消防气压给水设备的压力进行检查，发现问题及时协助贵单位处理。

The fire water storage level and consumption of fire water tanks, fire water tanks, and fire pressure water supply equipment are monitored annually Check the pressure of the anti air pressure water supply equipment and assist your unit in dealing with any problems found in a timely manner.

d)气体灭火系统gas fire extinguishing system

d)-1 检查保养气体控制屏,保证正常运行。

Check and maintain the gas control panel to ensure normal operation.

d)-2检测气瓶的压力是否达到规范要求,有无泄漏现象。

Check whether the pressure of the gas cylinder meets the standard  requirements and whether there is any leakage.

d)-3检查试验手动和自动放气装置是否正常。

Check if the manual and automatic air release devices are functioning properly

during the experiment.

d)-4 测试自动报警系统中的烟、温感探测器同时动作, 检查气瓶的电磁

阀是否动作, 控制屏是否有放气信号,警铃、蜂鸣器是否动作。

Test the smoke and temperature detectors in the automatic alarm system to  operate simultaneously, and check the electromagnetic properties of the gas cylinder Whether the valve is activated, whether there is a deflation signal on the control screen, and whether the alarm bell and buzzer are activated.

d)-5每月检测控制屏的功能情况、气瓶压力是否正常。

Check the functionality of the control screen and whether the pressure of the  gas cylinder is normal every month.

d)-6每季度检查试验手动和自动放气装置。

Quarterly inspection and testing of manual and automatic air release devices.

d)-7每季度模拟进行烟、温感探测器动作，是否有放气信号，警铃、蜂鸣器是否动作

灵敏。

Simulate the operation of smoke and temperature detectors every quarter, check

for air release signals, and ensure the sensitivity of alarm bells and buzzers.

e) 防火分区fire compartment

e)-1检查防火门、防火卷帘门、电动防火门等的完好情况。

Check the integrity of fire doors, fire shutter doors, electric fire doors, etc. every

week.

e)-2每季度手动或自动启停防火卷帘门、电动防火门门禁自动释放试验。

Quarterly manual or automatic start stop fireproof rolling shutter doors and electric

fireproof door access control automatic release test.

f) 防排烟系统smoke control system

f)-1 每周检查送风、排烟机房工作环境以及送风机、排烟机、电源控制柜、送风阀、排烟阀等是否处于正常完好状态。

Every week, check the working environment of the air supply and exhaust room, as

well as whether the air supply fan, exhaust fan, power control cabinet, air supply

valve, exhaust valve, etc. are in normal and intact condition.

f)-2每半年手动或自动打开排烟阀、启/停送风机、排烟机查看其性能。

Every six months, manually or automatically open the smoke exhaust valve,

start/stop the air supply fan, and check the performance of the smoke exhaust fan.

f)-3每半年手动或自动方式关闭空调通风系统、电动防火阀试验，检查其性能。

Every six months, manually or automatically shut down the air conditioning and ventilation system, and conduct tests on the electric fire damper to check their performance.

g) 应急照明疏散指示Emergency lighting evacuation instructions

g)-1每周检查安全出口、疏散通道、重要场所的应急照明和疏散指示标志是否处于正常

完好使用状态。

Check weekly whether the emergency lighting and evacuation signs at safety

exits, evacuation routes, and important places are in normal and intact condition.

g)-2每月试验应急照明灯和疏散指示灯切断电源后是否能正常工作。

Every month, test whether the emergency lighting and evacuation indicator lights can work normally after cutting off the power supply.

h)其它other

h)-1每季度检查干粉灭火器的压力、重量、有效期等。必要时做喷射试验。

Check the pressure, weight, and expiration date of dry powder fire extinguishers

every quarter. If necessary, conduct a spray test.

h)-2每月检查集水坑排设备、自救逃生设备，消防电源及自动切换设备是否处于正常完

好状态。

Check the drainage equipment of the collection pit, self rescue and escape   equipment, fire power supply, and automatic switching equipment every month to ensure that they are in normal and intact condition.

h)-3每季度试验消防电源末端的切换功能。

Quarterly testing of the switching function at the end of the fire power supply.

5.1.2.3维护标准Maintain standards

a) 保证系统正常工作。

Ensure the normal operation of the system.

b) 维护质量必须符合经双方核定的竣工图纸的要求，并且满足现行消防规范的要求。

The maintenance quality must comply with the requirements of the approved  completion drawings by both parties and meet the requirements of current fire safety regulations.

c) 设备发生故障，维保公司接收到故障信息或接到使用方通知十二小时内派人到达现 场，二十四小时内检修解除故障。在确实没有配件的情况下应及时向贵单位汇报，并采取有效的应急措施，防止出现安全事故。

If the equipment malfunctions, the maintenance company will send personnel to the site within 12 hours upon receiving the fault information or notification from the user, and repair and resolve the fault within 24 hours. In the absence of accessories, it is necessary to report to your company in a timely manner and take effective emergency measures to prevent safety accidents.

d) 提供详细的月检、季检及年度试验报告，以方便万国数据中心备案。

Provide detailed monthly, quarterly, and annual test reports for the convenience of filing with the GDS Data Center.

四、建筑消防设施检查维修保养服务方式

Service mode for inspection, maintenance and upkeep of building fire protection facilities

## 5.2 消防责任人 Fire Protection Responsible Person

5.2.1贯彻执行消防法规，保障单位消防安全符合规定，掌握本单位的消防安全情况；

Implement fire safety regulations, ensure that unit fire safety complies with regulations, and grasp the fire safety situation of the unit;

5.2.2将消防工作与本单位的生产、科研、经营、管理等活动统筹安排，批准实施年度消防工作计划；

Coordinate and arrange fire safety work with the production, scientific research, operation, management and other activities of the unit, and approve the implementation of the annual fire safety work plan;

5.2.3为本单位的消防安全提供必要的经费和组织保障；

Provide necessary funding and organizational support for the fire safety of our unit;

5.2.4确定逐级消防安全责任，批准实施消防安全制度和保障消防安全的操作规程；

Determine the hierarchical fire safety responsibilities, approve the implementation of fire safety systems and operational procedures to ensure fire safety;

5.2.5组织防火检查，督促落实火灾隐患整改，及时处理涉及消防安全的重大问题；

Organize fire prevention inspections, supervise the implementation of fire hazard rectification, and promptly handle major issues related to fire safety;

5.2.6根据消防法规的规定建立专职消防队、义务消防队;

Establish dedicated and voluntary fire brigades in accordance with fire regulations;

5.2.7组织制定符合本单位实际的灭火和应急疏散预案，并实施演练。

Organize the development of fire extinguishing and emergency evacuation plans that are in line with the actual situation of the unit, and implement drills.

## 5.3 防火巡查人员（安保/运维技术员） Fire patrol personnel (security/operation and maintenance technicians)

5.3.1防火巡查人员由消防值班人员和保安人员担任。

The fire patrol personnel are composed of fire duty personnel and security personnel.

5.3.2防火巡查频次为每4小时一次,作业结束时还应对作业现场进行检查,消除遗留火种和可燃垃圾,重点加强夜晚的巡查;

The frequency of fire prevention inspections is once every 4 hours. At the end of the operation, the work site should also be inspected to eliminate any remaining sparks and combustible waste, with a focus on strengthening night patrols;

5.3.3防火巡查时应携带手机等通讯工具,发现火灾应立即报火警并实施扑救。防火巡查应包括下列内容:

During fire inspections, communication tools such as mobile phones should be carried. If a fire is found, the fire alarm should be immediately reported and firefighting should be carried out. Fire inspection should include the following contents:

5.3.3.1用火、用电有无违章情况;

Whether there are any violations of fire and electricity usage regulations;

5.3.3.2安全出口、疏散通道是否畅通, ;安全疏散指示标志、应急照明是否完好;

Whether the safety exits and evacuation routes are unobstructed; Whether the safety evacuation signs and emergency lighting are intact;

5.3.3.3常闭式防火门是否处于关闭状态,防火卷帘下是否堆放物品;

Is the normally closed fire door in a closed state, and are there any items piled up under the fire shutter;

5.3.3.4消防设施、器材是否完整有效。消防安全标志是否完好清晰;

Whether the fire-fighting facilities and equipment are complete and effective. Whether the fire safety signs are intact and clear;

5.3.3.5消防安全重点部位的人员在岗情况;

Personnel on duty in key areas of fire safety;

5.3.4其他消防安全情况。

Other fire safety situations.

5.3.5防火巡查人员当及时纠正违章行为,妥善处置火灾隐患。无法处置时,应当立即报告。

Fire inspection personnel should promptly correct violations and properly handle fire hazards. When unable to handle, it should be reported immediately.

5.3.6防火巡查人员应填写《每日防火巡查记录表》,巡查人员及其主管人员应当在巡查记录上签名。

Fire inspection personnel should fill out the "Daily Fire Inspection Record Form", and the inspection personnel and their supervisors should sign on the inspection record.

5.3.7发现火灾隐患应及时填写火灾隐患整改通知,并督促整改。

If a fire hazard is discovered, a fire hazard rectification notice should be promptly filled out and the rectification should be urged.

## 5.4 消防控制室人员 Fire control room personnel

5.4.1应实行每日24 h专人值班制度，每班不应少于2人，值班人员应持有消防控制室操作职业资格证书；

A 24-hour dedicated duty system should be implemented, with no less than 2 people per shift. The duty personnel should hold a professional qualification certificate for operating the fire control room;

5.4.2消防设施日常维护管理应符合GB 25201的要求；

The daily maintenance and management of fire-fighting facilities should comply with the requirements of GB 25201;

5.4.3应确保火灾自动报警系统、灭火系统和其他联动控制设备处于正常工作状态，

It should be ensured that the automatic fire alarm system, fire extinguishing system, and other linkage control equipment are in normal working condition;

5.4.4应确保高位消防水箱、消防水池、气压水罐等消防储水设施水量充足，确保消防泵出水管阀门、自动喷水灭火系统管道上的阀门常开；确保消防水泵、防排烟风机、防火卷帘等消防用电设备的配电柜启动开关处于自动位置(通电状态)。

It should be ensured that the high-level fire water tank, fire water tank, pressure water tank and other fire water storage facilities have sufficient water volume, and that the valves on the fire pump outlet pipe and automatic sprinkler system pipeline are always open; Ensure that the starting switch of the distribution cabinet for fire-fighting electrical equipment such as fire pumps, smoke exhaust fans, and fire-resistant rolling shutters is in the automatic position (powered on state).

5.4.5消防控制室的值班应急程序应符合下列要求：

The emergency procedures for duty in the fire control room should meet the following requirements:

1)接到火灾警报后，值班人员应立即以最快方式确认；

After receiving a fire alarm, the on duty personnel should immediately confirm it in the fastest way possible;

2)火灾确认后，值班人员应立即确认火灾报警联动控制开关处于自动状态，同时拨打“119”报警，报警时应说明着火单位地点、起火部位、着火物种类、火势大小、报警人姓名和联系电话；

After confirming the fire, the on duty personnel should immediately confirm that the fire alarm linkage control switch is in automatic mode, and call "119" to report the fire. When reporting the fire, the location of the unit on fire, the location of the fire, the type of object on fire, the size of the fire, the name and contact phone number of the caller should be explained;

3)值班人员应立即启动单位内部应急疏散和灭火预案，并同时报告单位负责人。

The on duty personnel should immediately activate the internal emergency evacuation and fire extinguishing plan of the unit, and report to the unit leader at the same time.

5.4.6消防控制室工作人员应严格遵守消防控制室的各项安全操作规程和各项消防安全管理制度。

The staff of the fire control room should strictly abide by the various safety operating procedures and fire safety management systems of the fire control room.

5.4.7消防控制室应当实行每日24小时专人值班制度，确保及时发现并准确处置火灾和故障报警。

The fire control room should implement a 24-hour dedicated duty system to ensure timely detection and accurate handling of fire and fault alarms.

5.4.8掌握和了解消防设施的运行、误报警、故障等有关情况。

Master and understand the operation, false alarms, malfunctions, and other related situations of fire-fighting facilities.

5.4.9熟练掌握《消防控制室管理及应急程序》，火灾情况下能够按照程序开展灭火救援工作。

Proficient in "Fire Control Room Management and Emergency Procedures", able to carry out firefighting and rescue work according to procedures in case of fire.

5.4.10消防控制室工作人员应按时上岗，并做好交接班工作，接班人员未到岗前交班人员不得擅自离岗。

The staff in the fire control room should be on duty on time and do a good job of handover. The handover personnel shall not leave their posts without authorization before the handover personnel arrive.

5.4.11消防控制室工作人员应按时上岗，并坚守岗位，尽职尽责，不得脱岗、替岗、睡岗，严禁值班前饮酒或在值班时进行娱乐活动，因确有特殊情况不能到岗的，应提前向单位主管领导请假，经批准后，由同等职务的人员代替值班。

The staff of the fire control room should be on duty on time, stick to their posts, fulfill their duties, and shall not leave their posts, take over their posts, or sleep on duty. It is strictly prohibited to drink alcohol before duty or engage in recreational activities during duty. If there are special circumstances that prevent them from coming to work, they should ask for leave from the unit's supervisor in advance. After approval, an equivalent position personnel can replace the on duty.

5.4.12应在消防控制室的入口处设置明显的标志；消防控制室应设置火灾事故应急照明、灭火器等消防器材，并配备相应的通讯联络工具。

Clear signs should be set up at the entrance of the fire control room; The fire control room should be equipped with emergency lighting, fire extinguishers and other fire-fighting equipment for fire accidents, and equipped with corresponding communication tools.

5.4.13消防控制室工作人员要爱护消防控制室的设施，保持控制室内的卫生。

The staff in the fire control room should take good care of the facilities and maintain the cleanliness of the control room.

5.4.14严禁无关人员进入消防控制室，随意触动设备。

Unauthorized personnel are strictly prohibited from entering the fire control room and touching equipment at will.

5.4.15消防控制室内严禁存放易燃易爆危险物品和堆放与设备运行无关的物品或杂物，严禁与消防控制室无关的电气线路与管道穿过。

Flammable and explosive dangerous goods, as well as items or debris unrelated to equipment operation, are strictly prohibited from being stored in the fire control room. Electrical circuits and pipelines unrelated to the fire control room are also strictly prohibited from passing through.

5.4.16消防控制室内严禁吸烟或动用明火。

Smoking or the use of open flames is strictly prohibited in the fire control room.

5.4.17值班人员应取得国家《消防设施操作员》四级及以上资格证书。

The on duty personnel should obtain a Level 4 or higher qualification certificate from the National Fire Facility Operator.

5.4.18消防控制室值班人员应配备以下装备并确保完整好用；消防腰斧、手报复位钥匙、灭火器（1kg）、防毒面具（自救呼吸器）、强力探照灯、消防扳手、爆闪肩灯。

The duty personnel in the fire control room should be equipped with the following equipment and ensure its completeness and usability; Fire waist axe, manual reset key, fire extinguisher (1kg), gas mask (self rescue respirator), powerful searchlight, fire wrench, and flashing shoulder light.

5.4.19消防控制室设置以下几种记录本，以记录有关值班情况；《消防控制室值班记录》、《建筑消防设施故障处理记录》、《建筑消防设施故障维修记录表》等记录。

The fire control room is equipped with the following types of record books to record relevant duty situations; Records such as "Duty Record of Fire Control Room", "Fault Handling Record of Building Fire Protection Facilities", "Maintenance Record Form of Building Fire Protection Facilities", etc.

5.4.20消防控制室交接班时，前后两班人员均应在场，在认真填写完值班交接班记录，确认现场物品无损坏、丢失并在值班交接记录上签字后，交班者方可离开。

When handing over the shift in the fire control room, both the front and back shift personnel should be present. After carefully filling out the shift handover record, confirming that there is no damage or loss of items on site, and signing on the shift handover record, the handover personnel can leave.

5.4.21遵守控制室的各项规章制度。

Comply with the rules and regulations of the control room.

5.4.22熟悉和掌握本系统的工作原理和操作规程，熟悉各种按键的功能，能够熟练操作。

Familiar with and proficient in the working principle and operating procedures of this system, familiar with the functions of various buttons, and able to operate proficiently.

5.4.23应当在岗在位，认真记录控制器日运行情况，每日检查火灾报警控制器的自检、消音、复位功能以及主备电源切换功能，消防联动控制器的运行状况，并认真填写《消防控制室值班记录》。

Should be on duty, carefully record the daily operation of the controller, check the self checking, silencing, resetting functions of the fire alarm controller, as well as the main and backup power switching functions, and the operation status of the fire linkage controller on a daily basis, and carefully fill out the "Fire Control Room Duty Record".

5.4.24及时发现和处理设备故障，并填写《建筑消防设施故障维修记录表》。

Promptly detect and handle equipment failures, and fill out the "Building Fire Protection Facility Failure Maintenance Record Form".

## 5.5 消防管理负责人 Fire Management Manager

5.5.1拟订年度消防工作计划，组织实施日常消防安全管理工作；

Develop an annual fire safety work plan and organize the implementation of daily fire safety management work;

5.5.2组织制订消防安全制度和保障消防安全的操作规程并检查督促其落实；

Organize the formulation of fire safety regulations and operational procedures to ensure fire safety, and inspect and supervise their implementation;

5.5.3拟订消防安全工作的资金投入和组织保障方案；

Develop funding and organizational support plans for fire safety work;

5.5.4组织实施防火检查和火灾隐患整改工作；

Organize and implement fire prevention inspections and fire hazard rectification work;

5.5.5组织实施对本单位消防设施、灭火器材和消防安全标志的维护保养，确保其完好有效，确保疏散通道和安全出口畅通；

Organize and implement maintenance and upkeep of the fire protection facilities, firefighting equipment, and fire safety signs of the unit, ensuring their integrity and effectiveness, and ensuring smooth evacuation routes and safety exits;

5.5.6组织管理专职消防队和义务消防队；

Organize and manage dedicated fire brigades and volunteer fire brigades;

5.5.7在员工中组织开展消防知识、技能的宣传教育和培训，组织灭火和应急疏散预案的实施和演练；

Organize the promotion, education, and training of fire safety knowledge and skills among employees, and organize the implementation and drills of fire extinguishing and emergency evacuation plans;

5.5.8单位消防安全责任人委托的其他消防安全管理工作。

Other fire safety management tasks entrusted by the unit's fire safety responsible person.

消防安全管理人应当定期向消防安全责任人报告消防安全情况，及时报告涉及消防安全的重大问题。未确定消防安全管理人的单位，前款规定的消防安全管理工作由单位消防安全责任人负责实施。

The fire safety manager shall regularly report the fire safety situation to the fire safety responsible person and promptly report major issues related to fire safety. For units without a designated fire safety manager, the fire safety management work specified in the preceding paragraph shall be implemented by the unit's fire safety responsible person.

6 管理要求Management requirements

## 6.1 人员管理staff management

## 6.1.1消防安全责任人Fire safety responsible person

6.1.1.1每月至少组织开展一次防火检查，督促落实火灾隐患整改。高层公共建筑应每半个月至少开展一次防火检查。

Organize at least one fire prevention inspection per month to supervise the implementation of fire hazard rectification. High rise public buildings should undergo fire safety inspections at least once every two weeks.

6.1.1.2每月组织召开消防安全例会，研究本单位消防工作，及时处理涉及消防安全的重大问题。

Organize monthly fire safety meetings to study the fire safety work of the unit and promptly address major issues related to fire safety.

6.1.2消防安全管理人Fire Safety Manager

6.1.2.1每月组织实施防火检查和火灾隐患整改。

Organize monthly fire inspections and rectify fire hazards.

6.1.2.2每年至少对本单位消防设施、灭火器材和消防安全标志进行一次全面检测，确保其完好有效和处于正常运行状态；确保疏散通道和安全出口的畅通。

Conduct a comprehensive inspection of the fire protection facilities, firefighting equipment, and fire safety signs of our unit at least once a year to ensure their integrity, effectiveness, and normal operation; Ensure smooth evacuation routes and safety exits.

每月组织编制消防工作情况，向消防安全责任人报告并存档，涉及消防安全的重大问题应及时报告。

Organize monthly compilation of fire safety work status, report to the fire safety responsible person and archive, and promptly report major issues related to fire safety.

6.1.3消防控制室值班人员职责Responsibilities of duty personnel in the fire control room

6.1.3.1 新版《管理要求》中消防控制室值班人员职责根据《消防设施操作员》（职业编码：4-07-05-04）、《建筑消防设施的维护管理》等规定内容整合而成。

The responsibilities of the on duty personnel in the fire control room in the new version of the "Management Requirements" are integrated based on regulations such as "Fire Facility Operators" (occupation code: 4-07-05-04) and "Maintenance and Management of Building Fire Facilities".

6.1.3.2 并结合实际突破性要求与外包服务单位签订劳务合同，避免出现临时招聘安排不具备消防设施操作证的人员上岗的情况。

And based on practical breakthrough requirements, sign labor contracts with outsourcing service units to avoid the situation of temporary recruitment and arrangement of personnel without fire protection facility operation certificates.

6.1.3.3强调劳动合同签订、持证上岗

Emphasize the signing of labor contracts and certification for employment.

6.1.3.4与单位(含外包服务单位)签订劳务合同，经专业培训考核后持证上岗，应掌握火灾自动报警系统和消防设施联动控制系统的功能原理及操作规程，熟练操作工作单位的消防设施设备。

Sign a labor contract with the unit (including outsourcing service units), undergo professional training and assessment, and hold a certificate to work. They should master the functional principles and operating procedures of the fire automatic alarm system and the linkage control system of fire protection facilities, and be proficient in operating the fire protection facilities and equipment of the work unit.

6.1.3.5设有集中报警系统及控制中心报警系统消防控制室的值班人员应持有中级及以上的消防设施操作证。

The on duty personnel in the fire control room equipped with centralized alarm system and control center alarm system should hold intermediate or above fire protection facility operation certificate.

6.1.4 员工消防安全职责

Employee fire safety responsibilities

6.1.4.1员工需遵守单位消防安全制度、掌握基本消防技能外，还需承担自检自查、相互监督的职责。

Employees are required to comply with the unit's fire safety regulations, master basic fire safety skills, and also undertake the responsibilities of self inspection, self-examination, and mutual supervision.

6.1.4.2到岗、离岗之前自检自查

Self inspection before arrival and departure.

6.1.4.3每日到岗后及离岗前应检查本岗位工作设施、设备、场地、电源插座、电气设备的使用状态等，发现隐患及时处置并向消防工程师报告。

After arriving at work and before leaving, the working facilities, equipment, site, power sockets, and electrical equipment of the position should be inspected daily. Any hidden dangers should be promptly dealt with and reported to the fire engineer.

6.1.5 员工相互监督Employee mutual supervision

6.1.5.1 监督其他人员遵守消防安全管理制度，制止吸烟、使用大功率电器等不利于消防安全的行为。

Supervise other personnel to comply with the fire safety management system, and stop behaviors that are detrimental to fire safety, such as smoking and using high-power electrical appliances.

6.1.5.2人员密集场所现场员工应在发生火灾时立即组织、引导在场人员疏散。

Employees in densely populated areas should immediately organize and guide the evacuation of personnel in the event of a fire.

## 6.2 微型消防站管理Micro fire station management

6.2.1单位应根据法律法规建立微型消防站，定期组织训练演练，积极参与消防安全区域联防联控，接受消防救援机构的指令调派，提高自防自救能力。

Units should establish micro fire stations in accordance with laws and regulations, regularly organize training and drills, actively participate in joint prevention and control of fire safety areas, accept instructions and dispatch from fire rescue agencies, and improve self-defense and self rescue capabilities.

6.2.2微型消防站职责

Responsibilities of Micro Fire Station

6.2.3根据相关标准、规定的要求和本单位所属行业、单位性质、规模等实际情况，配备符合要求的执勤用房、装备器材、办公用品，并落实相关人员。

According to relevant standards and regulations, as well as the actual situation of the industry, nature, and scale of the unit, equip duty rooms, equipment, and office supplies that meet the requirements, and assign relevant personnel.

6.2.4熟悉单位、场所平面布局、重点部位和固定消防设施等消防安全基本情况，快速参与灭火与应急救援工作。

Familiarize oneself with the basic fire safety situation of the unit, site layout, key areas, and fixed fire-fighting facilities, and quickly participate in firefighting and emergency rescue work.

6.2.5制定训练计划并组织实施，提高火灾扑救和应急救援的能力。

Develop a training plan and organize its implementation to enhance the ability to extinguish fires and provide emergency rescue.

6.2.6制定完善单位、场所灭火救援预案，定期组织消防演练。

Develop and improve fire extinguishing and rescue plans for units and places, and regularly organize fire drills.

6.2.7开展防火巡查和消防宣传教育、业务培训。

Carry out fire prevention inspections, fire prevention publicity and education, and business training.

6.2.8结合本单位实际情况，建立健全应急响应机制，接受属地消防救援机构统一管理。

Based on the actual situation of our unit, establish and improve emergency response mechanisms, and accept unified management by local fire rescue agencies.

## 6.3消防法律责任Fire legal responsibility

6.3.1《中华人民共和国消防法》第六十条 单位违反本法规定，有下列行为之一的，责令改正，处五千元以上五万元以下罚款：

Article 60 of the Fire Protection Law of the People's Republic of China: If a unit violates the provisions of this Law and commits any of the following acts, it shall be ordered to make corrections and fined not less than 5000 yuan but not more than 50000 yuan:

消防设施、器材或者消防安全标志的配置、设置不符合国家标准、行业标准，或者未保持完好有效的

The configuration and installation of fire-fighting facilities, equipment, or fire safety signs do not comply with national or industry standards, or are not maintained in good condition and effectiveness

损坏、挪用或者擅自拆除、停用消防设施、器材的；

Damaging, misappropriating, or illegally dismantling or deactivating fire-fighting facilities and equipment;

占用、堵塞、封闭疏散通道、安全出口或者有其他妨碍安全疏散行为的；

Occupying, blocking, sealing evacuation routes, emergency exits, or engaging in other behaviors that hinder safe evacuation;

埋压、圈占、遮挡消火栓或者占用防火间距的；

Burial, enclose, block fire hydrants or occupy fire separation distances;

占用、堵塞、封闭消防车通道，妨碍消防车通行的；

Occupying, blocking, or sealing fire truck passages, obstructing the passage of fire trucks;

人员密集场所在门窗上设置影响逃生和灭火救援的障碍物的；

Setting up obstacles on doors and windows in densely populated areas that affect evacuation and firefighting rescue;

对火灾隐患经公安机关消防机构通知后不及时采取措施消除的。

Failure to take timely measures to eliminate fire hazards after being notified by the public security fire department.

6.3.2个人有前款第二项、第三项、第四项、第五项行为之一的，处警告或者五百元以下罚款。

Individuals who engage in any of the behaviors listed in the second, third, fourth, or fifth items of the preceding paragraph shall be given a warning or fined up to 500 yuan.

6.3.3有本条第一款第三项、第四项、第五项、第六项行为，经责令改正拒不改正的，强制执行，所需费用由违法行为人承担。

If a person commits an act under the third, fourth, fifth, or sixth items of the first paragraph of this article and refuses to correct it after being ordered to do so, compulsory execution shall be carried out, and the necessary expenses shall be borne by the offender.

6.3.4《消防安全责任制实施办法》

Implementation Measures for Fire Safety Responsibility System.

6.3.5《消防安全责任制实施办法》第二十八条 因消防安全责任不落实发生一般及以上火灾事故的，依法依规追究单位直接责任人、法定代表人、主要负责人或实际控制人的责任，对履行职责不力、失职渎职的政府及有关部门负责人和工作人员实行问责，涉嫌犯罪的，移送司法机关处理。

Article 28 of the Implementation Measures for the Fire Safety Responsibility System stipulates that if a general or above fire accident occurs due to the failure to fulfill fire safety responsibilities, the direct responsible person, legal representative, main person in charge or actual controller of the unit shall be held accountable in accordance with laws and regulations. Government and relevant department heads and staff who fail to perform their duties effectively or neglect their duties shall be held accountable. Those suspected of committing crimes shall be transferred to judicial organs for handling.

（一般火灾是指造成3人以下死亡，或者10人以下重伤，或者1000万元以下直接财产损失的火灾）

(A general fire refers to a fire that causes less than 3 deaths, or less than 10 serious injuries, or direct property damage of less than 10 million yuan)

## 6.4 消防设备设施管理Fire equipment and facility management

6.2.1 消防设施设备的设计与配置

Design and configuration of fire-fighting facilities and equipment

6.2.1.1数据中心内部所有消防应急相关设施（消防水池、消防泵、消防管路、消火栓、灭火器、喷淋系统、烟感系统、手动报警系统、消防电话、消控室、消防广播、消防警铃、消防备用电源、应急照明、疏散逃生标志）必须遵照消防设计进行配备，确保消防设备设施能满足现场的消防需求。数据中心需完成《数据中心消防设备全量验收清单》。

All fire emergency related facilities within the data center (fire water pool, fire pump, fire pipeline, fire hydrant, fire extinguisher, sprinkler system, smoke detection system, manual alarm system, fire telephone, fire control room, fire broadcast, fire alarm bell, fire backup power supply, emergency lighting, evacuation signs) must be equipped in accordance with the fire protection design to ensure that the fire equipment and facilities can meet the on-site fire protection needs. The data center needs to complete "Full Acceptance Checklist for Fire Protection Equipment in the Data Center".

6.2.1.2防火门、逃生门、疏散楼梯、防火墙或其他防火分隔等，应满足消防设计要求，不得私自改动（如增加开口、改变门或分隔的材质等等）。

Fire doors, escape doors, evacuation stairs, firewalls, or other fire partitions should meet the requirements of fire protection design and should not be modified without authorization (such as adding openings, changing the material of doors or partitions, etc.).

6.2.1.3所有建筑物防雷系统应通过防雷验收，且每年必须进行定期检验，保证接地电阻合格，并留存有检测报告。

All building lightning protection systems must pass lightning protection acceptance and undergo regular inspections every year to ensure that the grounding resistance is qualified, and test reports must be retained.

6.2.2消防设备设施的日常检查和维护

Daily inspection and maintenance of fire-fighting equipment and facilities

6.2.2.1消防设备设施应一直处于启用状态。禁止将消防系统中的水电临时挪作它用。对消防设备设施进行停用或检维修时，应通知到消防安全管理人员，并采取必要的安全措施。

Firefighting equipment and facilities should always be in operation. It is prohibited to temporarily divert water and electricity from the fire protection system for other purposes. When stopping or repairing fire-fighting equipment and facilities, the fire safety management personnel should be notified and necessary safety measures should be taken.

6.2.2.2灭火器、消防栓应每月由安保团队进行检查，并填写《灭火器、消火栓、钢瓶、灭火弹、探火管点检表》。发现有异常或过期的消防器材，应及时进行更换。

Fire extinguishers and hydrants should be inspected monthly by the security team, and the "Fire Extinguisher, Fire Hydrant, Steel Cylinder, Fire Extinguishing Bullet, and Fire Detection Tube Inspection Form" should be filled out. If any abnormal or expired fire-fighting equipment is found, it should be replaced in a timely manner.

6.2.2.3数据中心委托第三方单位对消防设施进行维护保养和检测，应委托有资质的单位对数据中心内消防设施进行维护保养。维保频率不低于每月一次，每年对消防设施进行一次全面的检测，并保持《建筑物消防设施维护保养记录》、《建筑物消防设施检测记录》等资料。

The data center entrusts a third-party unit to maintain and inspect the fire protection facilities, and should entrust a qualified unit to maintain and repair the fire protection facilities in the data center. The maintenance frequency shall not be less than once a month, and a comprehensive inspection of fire protection facilities shall be conducted once a year, while maintaining records such as the "Building Fire Protection Facility Maintenance Record" and the "Building Fire Protection Facility Inspection Record".

6.2.2.4维保内容应覆盖所有消防设备设施，包括但不限于：报警系统、探测系统、排烟系统、室内外消火栓、灭火器、消防泵房、消防中控室、应急照明、疏散方向指示灯、防火分隔等。

The maintenance content should cover all fire-fighting equipment and facilities, including but not limited to: alarm system, detection system, smoke exhaust system, indoor and outdoor fire hydrants, fire extinguishers, fire pump room, fire control room, emergency lighting, evacuation direction indicator lights, fire separation, etc.

6.2.3 消防控制室管理

Fire Control Room Management

6.2.3.1应确保消防控制室的管理满足消防、保证值班的人数，确保火灾情况下有人能按操作规程及时、正确操作建筑消防设施。

It should be ensured that the management of the fire control room meets the requirements of firefighting and the number of people on duty, and that someone can operate the building's fire-fighting facilities in a timely and correct manner according to the operating procedures in case of a fire.

6.2.3.2消防控制室的值班人员和时间满足下列要求：

The duty personnel and time in the fire control room shall meet the following requirements:

a) 消防控制室实行每日24h值班制度。值班人员应通过消防行业特有工种职业技能鉴定，

持有初级技能以上等级的职业资格证书。

The fire control room implements a 24-hour daily duty system. The on duty personnel should pass the specialized occupational skill appraisal of the fire protection industry and hold a vocational qualification certificate at or above the level of primary skills.

b) 每班人员应不少于2人。值班人员对火灾报警控制器进行检查、接班、交班时，应填

写《消防控制室值班记录表》的相关内容。值班期间每2h记录一次消

防控制室内消防设备的运行情况，及时记录消防控制室内消防设备的火警或故障情况。

Each shift should have no less than 2 personnel. When the on duty personnel inspect, take over, and hand over the fire alarm controller, they should fill out the relevant content of the "Fire Control Room Duty Record Form". During the duty period, record the operation status of the fire-fighting equipment in the fire control room every 2 hours, and promptly record any fire alarms or malfunctions of the fire-fighting equipment in the fire control room.

c) 确保火灾自动报警系统、灭火系统和其他联动控制设备处于正常工作状态，不得将应

处于自动状态的设在手动状态。

Ensure that the automatic fire alarm system, fire extinguishing system, and other linkage control equipment are in normal working condition, and do not set those that should be in automatic mode to manual mode.

d) 正常工作状态下，不应将自动喷水灭火系统、防烟排烟系统和联动控制的防火卷帘等

防火分隔设施设置在手动控制状态。其他消防设施及其相关设备如设置在手动状态时，应有在火灾情况下迅速将手动控制转换为自动控制的可靠措施。

Under normal working conditions, fire separation facilities such as automatic sprinkler fire extinguishing systems, smoke prevention and exhaust systems, and fire shutters with linkage control should not be set in manual control mode. When other fire-fighting facilities and related equipment are set in manual mode, reliable measures should be taken to quickly switch from manual control to automatic control in case of a fire.

e) 消防控制室值班人员接到报警信号后，应按下列程序进行处理：

After receiving the alarm signal, the on duty personnel in the fire control room should

handle it according to the following procedures:

- 接到火灾报警信息后，以最快方式进行确认。

After receiving the fire alarm information, confirm it as soon as possible.

- 确认属于误报时，查找误报原因并填写附件《建筑消防设施故障维修记录表》。

When confirming that it is a false alarm, search for the cause of the false alarm and

fill out the attached "Building Fire Protection Facility Fault Maintenance Record Form".

- 火灾确认后，立即将火灾报警联动控制开关转入自动状态（处于自动状态的除

外），同时拨打“119”火警电话报警。

After confirming the fire, immediately turn the fire alarm linkage control switch to automatic mode (except for those in automatic mode), and call the "119" fire alarm number to report the fire.

- 立即启动单位内部灭火和应急疏散预案，同时报告单位消防安全责任人。单位消防安

全责任人接到报告后应立即赶赴现场。

Immediately activate the internal fire extinguishing and emergency evacuation plan

of the unit, and report to the unit's fire safety responsible person. The person in

charge of fire safety in the unit should immediately rush to the scene upon

receiving the report.

f) 消防控制室的安全管理信息、控制及显示要求应满足《消防控制室通用技术要求》

（GB 25506）的规定。

The safety management information, control, and display requirements of the fire control room shall comply with the provisions of the General Technical Requirements for Fire Control Rooms (GB 25506).

6.2.4 消防安全标志Fire safety signs

数据中心所有需要设置消防安全标志的场所，参照《消防安全标志 第1部分：标志》（GB 13495.1）、《消防安全标志设置要求》（GB 1530）执行。

All locations in the data center that require the installation of fire safety signs shall comply with the "Fire Safety Signs Part 1: Signs" (GB 13495.1) and "Requirements for the Installation of Fire Safety Signs" (GB 1530).

## 6.3 消防安全重点部位管理Management of key fire safety areas

6.3.1 数据中心柴油储存区域（日用油箱间、柴油储罐、电池间等）、配电房等为消防安全重点部位。

The diesel storage area (daily fuel tank room, diesel storage tank, battery room, etc.) and power distribution room in the data center are key areas for fire safety.

6.3.2 消防安全重点部位需要有负责人（消防工程师等）定时对重点位置进行巡查，发现问题及时上报处理。

Key fire safety areas require a responsible person (such as a fire engineer) to conduct regular inspections of these areas and promptly report any issues for resolution.

6.3.3 消防安全重点部位应设置明显的禁烟禁火等标示，非工作人员禁止进入消防安全重点部位。

Clear signs prohibiting smoking and fire should be set up in key fire safety areas, and non staff are prohibited from entering these areas.

6.3.4 消防安全重点部位管理人员应懂消防知识、清楚重点部位消防管理要求、检查要求、现场应急处置要求。

The management personnel of key fire safety areas should have knowledge of fire safety, be clear about the fire management requirements, inspection requirements, and on-site emergency response requirements of key areas.

6.3.5消防安全重点部位应每日进行安全巡查，主要检查事项如下：

Key fire safety areas should be inspected daily, with the following main inspection items:

a) 柴油储存部位，结合《日用油箱间日常防火检查表》内容进行检查，

重点对人员PPE，油品泄漏，搬运，静电，动火许可，消防器材、火灾隐患等进行日常

巡查,《防火巡查记录表》详见附件6。

The diesel storage area shall be inspected in accordance with the "Daily Fire  Prevention Inspection Checklist for Daily Fuel Tank Rooms" , with a focus on personnel PPE, oil leakage, handling, static electricity, hot work permits, fire-fighting equipment, fire hazards, and other daily inspections. Please refer to Attachment 6 for the "Fire Inspection Record Form".

b) 高低压配电室，结合《配电室日常防火检查表》内容进行检查，重点

对消防器材、入口、门与警示标识、出入口及孔洞、物品堆放、绝缘工器具进行日常

巡查。

The high and low voltage distribution room shall be inspected in accordance with the contents of the "Daily Fire Prevention Inspection Checklist for Distribution Room", with a focus on daily inspections of fire-fighting equipment, entrances, doors and warning signs, entrances and exits and holes, item stacking, and insulation tools.

6.3.6 电池间和日用油箱间进入前需进行除静电防护工作，防止因为人员自身带静电导致火灾或爆炸产生。

Before entering the battery room and daily fuel tank room, anti-static protection measures must be taken to prevent fires or explosions caused by personnel carrying static electricity.

## 6.4 动火作业及防火Hot work and fire prevention

6.4.1动火作业管理

Hot work management

6.4.1.1因工作需要在禁火区域内动用明火时，必须事先办理《动火作业许可证》，由专人监护，在确认无火灾、爆炸危险源后方可动火施工。

When using open flames in the prohibited fire area due to work needs, a "Hot Work Permit" must be obtained in advance, supervised by a dedicated person, and hot work construction can only be carried out after confirming that there are no fire or explosion hazards.

6.4.1.2动火施工人员应遵守消防安全规定，并落实相应的消防安全保护措施。

Hot work construction personnel should comply with fire safety regulations and implement corresponding fire safety protection measures.

6.4.1.3严禁在易燃易爆场所内使用明火, 如涉及易燃易爆物品作业场所，应有明显禁烟、火警标志，严禁吸烟。

It is strictly prohibited to use open flames in flammable and explosive places. If there are workplaces involving flammable and explosive materials, there should be obvious signs prohibiting smoking and fire alarms. Smoking is strictly prohibited.

6.4.1.4外来单位或人员进入，作业前应规定其进出数据中心的路径，保证施工或作业范围内的消防安全。

Foreign units or personnel entering the data center should have their entry and exit paths specified before starting work to ensure fire safety within the construction or operation scope.

6.4.1.5如进行电焊、气焊等具有火灾危险作业的人员和自动消防系统的操作人员，必须持证上岗，并遵守消防安全操作规程。

Personnel engaged in welding, gas welding, and other operations with fire hazards, as well as operators of automatic fire protection systems, must hold a certificate and comply with fire safety operating procedures.

6.4.2用电安全管理

Electricity safety management

6.4.2.1数据中心内严禁擅自乱拉、乱接电源线路，不得随意增设电器设备。如需改变或安装线路，必须由持合格证的电工负责。

It is strictly prohibited to randomly pull or connect power lines in the data center, and it is not allowed to add electrical equipment at will. If it is necessary to change or install the circuit, it must be the responsibility of a certified electrician.

6.4.2.2所涉及电源线路、电器设备应保持清洁，配电箱、立式配电柜内应保持干燥，不得有灰尘堆积，不准堆放物品。各电气设备的导线、接点、开关不得有断线、老化、裸露、破损。禁止使用不合格的保险装置，电气设施严禁超负荷运行。

The power lines and electrical equipment involved should be kept clean, and the distribution box and vertical distribution cabinet should be kept dry without dust accumulation or stacking of items. The wires, contacts, and switches of each electrical equipment must not be broken, aged, exposed, or damaged. The use of unqualified safety devices is prohibited, and electrical facilities are strictly prohibited from operating at overload.

6.4.2.3合理安装电气设备，做到安全操作，经常检查，及时维修，保证用电安全。

Reasonably install electrical equipment, ensure safe operation, regularly inspect, and promptly repair to ensure electrical safety.

6.4.2.4电气线路、电器设备必须由持合格证的电工进行安装、检查和维修保养，操作时必须严格遵守各项安全操作规程。

Electrical circuits and equipment must be installed, inspected, and maintained by certified electricians, and all safety operating procedures must be strictly followed during operation.

6.4.2.5凡电加热设备应落实专人负责操作和看管，离开时必须切断电源，禁止使用人取暖器。

All electric heating equipment should be operated and supervised by dedicated personnel. When leaving, the power must be cut off and the use of human heaters is prohibited.

6.4.2.6电气岗位/专业管理人员应经常组织对电气等关键设备进行巡检，及时清除粘附在设备上油污、粉尘等异物。

Electrical personnel/professional managers should regularly organize inspections of key electrical equipment and promptly remove foreign objects such as oil stains and dust adhering to the equipment.

6.4.2.7严禁在设备的电动机上、电箱开关内摆放物品。

It is strictly prohibited to place items on the electric motor of the equipment or inside the electrical box switch.

6.4.2.8所有的电器，插排必须带有漏电和过载保护器。

All electrical appliances and sockets must be equipped with leakage and overload protectors.

6.4.2.9严禁在电线、电缆上方堆放原辅材料、成品等易燃易爆物品。

It is strictly prohibited to stack flammable and explosive materials such as raw materials and finished products above wires and cables.

6.4.3除指定的吸烟区域，公司内部其他区域严禁吸烟。在指定吸烟区内，吸烟者应将烟头熄灭后再扔进烟灰缸中，禁止乱丢乱放, 指定吸烟区应配备灭火器、灭火器不得挪作它用。

Smoking is strictly prohibited in all areas within the company except for designated smoking areas. In designated smoking areas, smokers should extinguish their cigarette butts before throwing them into the ashtray. It is prohibited to litter them. Fire extinguishers should be equipped in designated smoking areas and should not be used for other purposes.

6.4.4 动火作业审批流程按工单要求编写动火作业申请表。

The approval process for hot work operations is to prepare a hot work application form according to the requirements of the work order.

## 6.5 消防安全检查及隐患整改Fire safety inspection and hidden danger rectification

6.5.1 日常安全检查

Daily safety checks

日常消防安全检查内容应包括：

The daily fire safety inspection should include:

- 用电、动火有无违章情况。

Whether there are any violations of electricity and hot work regulations.

- 安全出口、安全通道是否畅通，各种消防安全设施是否完好。

Whether the safety exits and passages are unobstructed, and whether various fire safety facilities are in good condition.

- 消防安全重点部位检查；火灾隐患的整改情况以及防范措施的落实情况。

Inspection of key fire safety areas; The rectification of fire hazards and the implementation of preventive measures.

- 消防（主机室）值班情况和设施运行、记录情况。

Firefighting (main engine room) duty situation and facility operation and recording situation.

- 消防车通道、消防水源情况；灭火器材配置及有效情况。

Fire truck access and fire water source situation; Fire extinguishing equipment configuration and effectiveness.

- 易燃易爆场所防火防爆措施落实情况及其他重要物资的防火安全情况。

The implementation of fire and explosion prevention measures in flammable and explosive places, as well as the fire safety situation of other important materials.

6.5.2 消防安全管理人员每月对所辖区域进行一次消防安全专项检查，将检查结果记录在案，落实整改措施，存档备案。

Fire safety management personnel conduct a special fire safety inspection of their jurisdiction once a month, record the inspection results, implement corrective measures, and file for record.

6.5.3 消防安全隐患整改

Rectification of fire safety hazards

检查中发现火灾隐患，检查人员应将记录检查结果，并告知相关部门/岗位/业务线人员，并追踪各现场单位对隐患的改善情况。

If a fire hazard is found during the inspection, the inspectors should record the inspection results and inform the relevant departments/positions/business line personnel, and track the improvement of the hazard by each on-site unit.

消防安全隐患整改方式分为：立即整改、限时整改和停工整改。

The rectification methods for fire safety hazards include immediate rectification, time limited rectification, and suspension of work rectification.

6.5.4 对下列违反消防安全规定的行为，消防安全管理人员应责令有关单位或个人立即整改并督促落实：

Fire safety management personnel shall order relevant units or individuals to immediately rectify and supervise the implementation of the following violations of fire safety regulations:

- 违章使用明火作业或者在消防安全重点部位吸烟、使用明火等违反禁令的。

Violating the prohibition of using open flames for work or smoking or using open

flames in key fire safety areas.

- 将安全出口上锁，遮挡或者占用、堆放物品影响疏散通道畅通的。

Locking, blocking, occupying, or stacking items at safety exits that affect the

smooth flow of evacuation routes.

- 消火栓、灭火器材被遮挡影响使用或者挪作他用的。

Fire hydrants and firefighting equipment that are obstructed, affecting their use or

diverted for other purposes.

- 常闭式防火门处于开启状态，防火门前、防火卷帘下堆放物品影响紧急逃生使用的。

The normally closed fire door is in an open state, and the stacking of items in front

of the fire door and under the fire shutter affects emergency evacuation use.

- 违章关闭消防设施、切断消防电源的。

Violating regulations by shutting down fire-fighting facilities and cutting off fire-

fighting power supply.

- 其他可以立即整改的。

Others that can be rectified immediately.

6.5.5 消防值班人员按要求填写《消防控制室值班记录》。

Firefighters on duty are required to fill out the 'Fire Control Room Duty Record'.

6.5.6 消防设施管理人员应每日对消防设施进行巡查。

Firefighting facility management personnel should conduct daily inspections of firefighting facilities.

6.5.7 各区域人员每日对所辖区域进行消防安全巡查。

Personnel from each region conduct daily fire safety inspections in their respective areas.

## 6.6 消防演习与培训Fire drills and training

6.6.1 全员参加每年度的消防演习（重点消防单位每半年一次）

制定全面的消防演习方案是确保所有人员在火灾发生时能够迅速、安全撤离的关键步骤。以下是一个详细的消防演习方案，涵盖了准备、实施和评估三个主要阶段：

All staff participate in the annual fire drill (key fire units conduct it every six months)

Developing a comprehensive fire drill plan is a key step in ensuring that all personnel can evacuate quickly and safely in the event of a fire. The following is a detailed fire drill plan, covering three main stages of preparation, implementation, and evaluation:

准备阶段Preparation stage

a) 成立演习小组成立演习小组

Establish a drill team Establish a drill team

组长（中心经理）：负责总体协调和指挥。

Team Leader (Center Manager): Responsible for overall coordination and command.

成员：包括消防工程师、运维主管、运维技术员、安保等。

Members: including fire engineers, operation and maintenance supervisors, operation and maintenance technicians, security personnel, etc.

b) 制定演习计划Develop exercise plan

目标：明确演习的具体目标，如提高人员疏散速度、检验消防设备的有效性等。

Objective: Clarify the specific objectives of the exercise, such as improving personnel

evacuation speed, testing the effectiveness of firefighting equipment, etc.

时间和地点：明确演习的具体时间和地点，尽量选择人员较多的时间段。

Time and location: Clearly specify the specific time and location of the exercise, and try to

choose a time period with a large number of personnel.

演习类型：明确是全员演习。

Exercise type: Clearly, it is a full staff exercise.

c) 准备消防设备Prepare firefighting equipment

灭火器、消防栓：检查设备是否完好，确保可用。

Fire extinguishers and hydrants: Check if the equipment is in good condition and ensure it

is usable.

报警系统：测试火警报警系统，确保其正常工作。

Alarm system: Test the fire alarm system to ensure its proper functioning.

d) 通知和培训Notification and Training

通知所有人员：提前通知所有参与演习的人员，说明演习的目的和重要性。

Notify all personnel: Notify all participants of the exercise in advance, explaining the purpose and importance of the exercise.

培训：对所有人员进行基本的消防安全培训，包括如何使用灭火器、如何疏散等。

Training: Provide basic fire safety training to all personnel, including how to use fire extinguishers, how to evacuate, etc.

实施阶段implementation phase

a) 启动演习（指挥组）

Launch exercise (command group)

触发报警：模拟火警，触发火警报警系统。

Trigger alarm: Simulate a fire alarm and trigger the fire alarm system.

广播通知：通过广播系统通知所有人员进行疏散。

Broadcast notification: Notify all personnel to evacuate through the broadcast system.

- 疏散人员（疏散组）

Evacuation personnel (evacuation team)

疏散路线：按照预定的疏散路线迅速、有序地疏散人员。

Evacuation route: Quickly and orderly evacuate personnel according to the predetermined evacuation route.

疏散指挥：楼层负责人和安全员引导人员疏散，确保没有人滞留。

Evacuation command: The floor manager and safety officer guide personnel to evacuate, ensuring that no one is stranded.

c) 应急响应（灭火组和人员物资抢救组）

Emergency response (fire extinguishing team and personnel and material rescue team)

灭火行动：模拟灭火，检查灭火器和消防栓的使用情况。

Firefighting action: Simulate firefighting and check the use of fire extinguishers and hydrants.

急救处理：模拟受伤人员的急救处理，测试急救员的应急能力。

First aid treatment: Simulate the first aid treatment of injured personnel and test the emergency capabilities of first responders.

d)集合和清点（外围警戒组）

Gather and Count (Peripheral Alert Group)

集合点：所有人员在预定的安全集合点集合。

Assembly point: All personnel gather at the designated safe assembly point.

清点人数：楼层负责人清点人数，确保所有人员安全撤离。

Counting the number of people: The floor manager counts the number of people to ensure the safe evacuation of all personnel.

评估阶段Evaluation phase

a)总结会议

Close meeting

召开总结会议：演习结束后，立即召开总结会议。

Convene a summary meeting: Immediately after the exercise, convene a summary meeting.

反馈意见：收集所有参与人员的反馈意见，记录演习中发现的问题。

Feedback: Collect feedback from all participants and record any issues discovered during the exercise.

b)评估报告

assessment report

编写评估报告：包括演习的成功之处和需要改进的地方。

Write an evaluation report: including the successes of the exercise and areas for improvement.

改进措施：制定改进措施，完善消防应急预案。

Improvement measures: Develop improvement measures and improve the fire emergency plan.

c)后续跟进

Follow up

整改问题：针对演习中发现的问题，进行整改和改进。

Rectification issues: Rectify and improve the problems discovered during the exercise.

定期演习：定期组织消防演习，确保所有人员熟悉应急程序。

Regular drills: Regularly organize fire drills to ensure that all personnel are familiar with emergency procedures.

示例时间表Example timetable

时间time	 活动activity	 负责人person in charge

09:00-09:15	成立演习小组，分配任务	中心经理

Establish a drill team and assign tasks    Centre Manager

09:15-09:30	检查消防设备	消防工程师

Check fire equipment        Fire Engineer

09:30-09:45	通知所有人员，进行培训	消防工程师

Notify all personnel to undergo training     Fire Engineer

10:00-10:05	触发报警，启动演习	中心经理

Trigger alarm, start exercise       Centre Manager

10:05-10:15	疏散人员，模拟灭火和急救运维技术员、安保

Evacuate personnel, simulate fire extinguishing and first aid Operations and

maintenance technicians, security personnel

10:15-10:20	集合和清点人数	运维主管

Gather and count the number of people   Operations Supervisor

10:20-10:30	总结会议，收集反馈	中心经理

Summarize the meeting and collect feedback    Centre Manager

10:30-11:00	编写评估报告，制定改进措施	消防工程师

Write an evaluation report and develop improvement measures Fire Engineer

通过详细的计划和严格的执行，消防演习可以有效提高人员的应急响应能力，确保在实际火灾发生时能够迅速、安全地进行疏散和救援。

Through detailed planning and strict execution, fire drills can effectively improve personnel's emergency response capabilities, ensuring that evacuation and rescue can be carried out quickly and safely in the event of an actual fire.

6.6.2全员应当接受消防安全专业培训及考试：（重点消防单位每半年一次）（以下人员需定期培训）

All staff should receive professional training and examination on fire safety: (Key fire units should receive training every six months) (The following personnel need regular training)

- 单位的消防安全责任人、消防安全管理人员、专职消防队员；

The fire safety responsible person, fire safety management personnel, and full-time firefighters of the unit;

- 建设工程消防设计和消防设施施工、安装、维修保养人员、消防产品的检验维修人员；

Personnel responsible for fire protection design and construction, installation, maintenance of fire protection facilities, as well as inspection and maintenance of fire protection products in construction projects;

- 从事易燃易爆危险品生产、储存、运输、销售、装卸的人员；

Personnel engaged in the production, storage, transportation, sales, loading and unloading of flammable and explosive dangerous goods;

- 自动消防系统的操作、管理人员；

Operators and managers of automatic fire protection systems;

- 从事电焊、气焊等具有火灾危险作业的人员；

Personnel engaged in welding, gas welding and other operations with fire hazards;

- 消防技术服务机构的执业人员；

Practitioners of fire technology service institutions;

- 其他依照有关规定需要培训的人员。

Other personnel who require training in accordance with relevant regulations.

前款第d项、第e项、第f项规定的人员应当经职业技能鉴定，取得职业资格，方可上岗。

The personnel specified in items d, e, and f of the preceding paragraph shall undergo

vocational skill appraisal and obtain professional qualifications before they can take up their posts.

6.6.2 消防管理负责人应对全员进行消防意识培训，如每年培训频率不低于2次（且不低于当地消防大队要求）。消防意识培训形式可采取课堂培训、网络在线培训或全员邮件/简报沟通，其中课堂培训每年至少进行1次。意识培训内容应包括但不限于：火灾危害、火灾隐患识别、消防设备设施识别、报警、逃生疏散等。

The person in charge of fire management shall provide fire awareness training to all staff, with a training frequency of no less than 2 times per year (and no less than the requirements of the local fire brigade). Fire safety awareness training can take the form of classroom training, online training, or all staff email/briefing communication, with classroom training conducted at least once a year. The content of awareness training should include but not limited to: fire hazards, identification of fire hazards, identification of fire-fighting equipment and facilities, alarm, evacuation, etc.

7 附件Attachments

- 无None